## E1L-1N
Panel Schedule
Panel: E1L-1N | [16 empty] | Voltage (L-N): | 277
Voltage: 480Y/277 |  |  | Mains: MLO |  | Loads (VA) | [6 empty] | Loc: 1ST FL ELEC RM |  |  | AIC: 14K |  | Demand Factors:
Amps: 50 | Wires: 4 |  | Phase: 3 | [8 empty] | Mounting: SURFACE |  |  |  |  | Ltg: | 1.25
Branch Circuit | Amp | P | Description | Cir | Ltg |  | Recept | Motor | Lg Motor | Equip |  | Cir | Description | P | Amp | Branch Circuit | Recept(<10kVA): | 1
3/4" C/3#10+1#10GRD | 30 | 3 | XFMR T-5 | 1 | 1250 | 1576 | 360 |  |  | 1440 |  | 2 | LTG: MULTI-PURPOSE | 1 | 20 | 3/4" C/2#12+1#12GRD | Recept(>10kVA): | 0.5
- | - | - | - | 3 |  | 963 |  |  |  | 1920 |  | 4 | LTG: STAIRWELL | 1 | 20 | 3/4" C/2#12+1#12GRD | Motor: | 1
- | - | - | - | 5 |  | 1272 |  |  |  | 2580 |  | 6 | LTG: EAST CONCOURSE | 1 | 20 | 3/4" C/2#12+1#12GRD | Lg Motor: | 1.25
3/4" C/2#12+1#12GRD | 20 | 1 | LTG: MAIN LOBBY | 7 | 1245 | [5 empty] | 2770 | 8 | FIRE ALARM PANEL | 1 | 20 | 3/4" C/2#12+1#12GRD | Equip: | 1
3/4" C/2#12+1#12GRD | 20 | 1 | LTG: GRND FL CORRIDOR | 9 | 315 | [6 empty] | 10 | SPARE | 1 | 20 | -
- | 20 | 1 | SPARE | 11 | [7 empty] | 12 | SPARE | 1 | 20 | -
- | 20 | 1 | SPARE | 13 | [7 empty] | 14 | SPARE | 1 | 20 | - | Recept Demand VA:
- | - | 1 | SPACE | 15 | [7 empty] | 16 | SPACE | 1 | - | - |  | Phase A | Phase B | Phase C | Total
- | - | 1 | SPACE | 17 | [7 empty] | 18 | SPACE | 1 | - | - | Total VA: | 360 | 0 | 0 | 360
|  |  |  | 19 | [7 empty] | 20 |  |  |  |  | First 10kVA | 360 | 0 | 0 | 360
|  |  |  | 21 | [7 empty] | 22 |  |  |  |  | Remaining VA: | 0 | 0 | 0 | 0
|  |  |  | 23 | [7 empty] | 24
|  |  |  | 25 | [7 empty] | 26
|  |  |  | 27 | [7 empty] | 28
|  |  |  | 29 | [7 empty] | 30
|  |  |  | 31 | [7 empty] | 32
|  |  |  | 33 | [7 empty] | 34
|  |  |  | 35 | [7 empty] | 36
|  |  |  | 37 | [7 empty] | 38
|  |  |  | 39 | [7 empty] | 40
|  |  |  | 41 | [7 empty] | 42
Connected Load Phase A: (A) |  |  | 31.1949 |  | 4071 |  | 360 | 0 | 0 | 4210 |  |  | Demand Load Phase A: (A) | 34.8691
Connected Load Phase B: (A) |  |  | 11.5451 |  | 1278 |  | 0 | 0 | 0 | 1920 |  |  | Demand Load Phase B: (A) | 12.6986
Connected Load Phase C: (A) |  |  | 13.9061 |  | 1272 |  | 0 | 0 | 0 | 2580 |  |  | Demand Load Phase C: (A) | 15.0542
Total VA: | 17346.25
Load: (A) | 20.8739
25% Growth: (A) | 26.0924

## E1P-1N
Panel Schedule
Panel: E1P-1N | [16 empty] | Voltage (L-N): | 120
Voltage: 208Y/120 |  |  | Mains: MCB |  | Loads (VA) | [6 empty] | Loc: 1ST FL ELEC RM |  |  | AIC: 10K |  | Demand Factors:
Amps: 50 | Wires: 4 |  | Phase: 3 | [8 empty] | Mounting: SURFACE |  |  |  |  | Ltg: | 1.25
Branch Circuit | Amp | P | Description | Cir | Ltg | Recept |  | Motor | Lg Motor | Equip |  | Cir | Description | P | Amp | Branch Circuit | Recept(<10kVA): | 1
3/4" C/2#12+1#12GRD | 20 | 1 | LTG: EXTERIOR CANOPY | 1 | 1250 |  | 360 |  |  |  |  | 2 | REC: ELECTRICAL CLOSET | 1 | 20 | 3/4" C/2#12+1#12GRD | Recept(>10kVA): | 0.5
3/4" C/2#12+1#12GRD | 20 | 1 | DOOR HOLD OPENS | 3 | [5 empty] | 360 | 180 | 4 | DOOR HOLD OPENS: 2ND | 1 | 20 | 3/4" C/2#12+1#12GRD | Motor: | 1
3/4" C/2#12+1#12GRD | 20 | 1 | DOOR HOLD OPENS | 5 | [5 empty] | 180 | 1200 | 6 | CARD READER CNTRL PNL | 1 | 20 | 3/4" C/2#12+1#12GRD | Lg Motor: | 1.25
3/4" C/2#12+1#12GRD | 20 | 1 | MED GAS ALARM PANEL | 7 | [5 empty] | 240 | 1200 | 8 | SECURITY POWER PANEL | 1 | 20 | 3/4" C/2#12+1#12GRD | Equip: | 1
3/4" C/2#12+1#12GRD | 20 | 1 | DOOR HOLD OPENS | 9 | [5 empty] | 180 | 1200 | 10 | SECURITY POWER PANEL | 1 | 20 | 3/4" C/2#12+1#12GRD
- | 20 | 1 | SPARE | 11 | [6 empty] | 1200 | 12 | CARD READER CNTRL PNL | 1 | 20 | 3/4" C/2#12+1#12GRD
- | - | 1 | SPACE | 13 | [7 empty] | 14 | SPACE | 1 | - |  | Recept Demand VA:
- | - | 1 | SPACE | 15 | [7 empty] | 16 | SPACE | 1 | - |  |  | Phase A | Phase B | Phase C | Total
- | - | 1 | SPACE | 17 | [7 empty] | 18 | SPACE | 1 | - |  | Total VA: | 360 | 0 | 0 | 360
|  |  |  | 19 | [7 empty] | 20 |  |  |  |  | First 10kVA | 360 | 0 | 0 | 360
|  |  |  | 21 | [7 empty] | 22 |  |  |  |  | Remaining VA: | 0 | 0 | 0 | 0
|  |  |  | 23 | [7 empty] | 24
|  |  |  | 25 | [7 empty] | 26
|  |  |  | 27 | [7 empty] | 28
|  |  |  | 29 | [7 empty] | 30
|  |  |  | 31 | [7 empty] | 32
|  |  |  | 33 | [7 empty] | 34
|  |  |  | 35 | [7 empty] | 36
|  |  |  | 37 | [7 empty] | 38
|  |  |  | 39 | [7 empty] | 40
|  |  |  | 41 | [7 empty] | 42
Connected Load Phase A: (A) |  |  | 25.4167 |  | 1250 | 360 |  | 0 | 0 | 1440 |  |  | Demand Load Phase A: (A) | 28.0208
Connected Load Phase B: (A) |  |  | 16 |  | 0 | 0 |  | 0 | 0 | 1920 |  |  | Demand Load Phase B: (A) | 16
Connected Load Phase C: (A) |  |  | 21.5 |  | 0 | 0 |  | 0 | 0 | 2580 |  |  | Demand Load Phase C: (A) | 21.5
Total VA: | 7862.5
Load: (A) | 21.8403
25% Growth: (A) | 27.3003

## E1L-2N
Panel Schedule
Panel: E1L-2N | [15 empty] | Voltage (L-N): | 277
Voltage: 480Y/277 |  |  | Mains: MLO |  | Loads (VA) | [5 empty] | Loc: 2ND FL ELEC RM |  |  | AIC: 14K |  | Demand Factors:
Amps: 50 | Wires: 4 |  | Phase: 3 | [7 empty] | Mounting: SURFACE |  |  |  |  | Ltg: | 1.25
Branch Circuit | Amp | P | Description | Cir | Ltg |  | Recept | Motor | Lg Motor | Equip | Cir | Description | P | Amp | Branch Circuit | Recept(<10kVA): | 1
3/4" C/2#12+1#12GRD | 20 | 1 | LTG: EGRESS | 1 | 786 | 654 |  |  |  |  | 2 | LTG: MECHANICAL RM | 1 | 20 | 3/4" C/2#12+1#12GRD | Recept(>10kVA): | 0.5
3/4" C/2#12+1#12GRD | 20 | 2 | FIREMAN'S OUTLET | 3 |  |  | 3840 |  |  |  | 4 | SPARE | 1 | 20 | - | Motor: | 1
- | - | - | - | 5 |  |  | 3840 |  |  |  | 6 | SPARE | 1 | 20 | - | Lg Motor: | 1.25
- | 20 | 1 | SPARE | 7 | [6 empty] | 8 | SPARE | 1 | 20 | - | Equip: | 1
- | 20 | 1 | SPARE | 9 | [6 empty] | 10 | SPARE | 1 | 20 | -
- | 20 | 1 | SPARE | 11 | [6 empty] | 12 | SPARE | 1 | 20 | -
- | - | 1 | SPACE | 13 | [6 empty] | 14 | SPACE | 1 | - | - | Recept Demand VA:
- | - | 1 | SPACE | 15 | [6 empty] | 16 | SPACE | 1 | - | - |  | Phase A | Phase B | Phase C | Total
- | - | 1 | SPACE | 17 | [6 empty] | 18 | SPACE | 1 | - | - | Total VA: | 0 | 3840 | 3840 | 7680
|  |  |  | 19 | [6 empty] | 20 |  |  |  |  | First 10kVA | 0 | 3840 | 3840 | 7680
|  |  |  | 21 | [6 empty] | 22 |  |  |  |  | Remaining VA: | 0 | 0 | 0 | 0
|  |  |  | 23 | [6 empty] | 24
|  |  |  | 25 | [6 empty] | 26
|  |  |  | 27 | [6 empty] | 28
|  |  |  | 29 | [6 empty] | 30
|  |  |  | 31 | [6 empty] | 32
|  |  |  | 33 | [6 empty] | 34
|  |  |  | 35 | [6 empty] | 36
|  |  |  | 37 | [6 empty] | 38
|  |  |  | 39 | [6 empty] | 40
|  |  |  | 41 | [6 empty] | 42
Connected Load Phase A: (A) |  |  | 5.1986 |  | 1440 |  | 0 | 0 | 0 | 0 |  | Demand Load Phase A: (A) | 6.4982
Connected Load Phase B: (A) |  |  | 13.8628 |  | 0 |  | 3840 | 0 | 0 | 0 |  | Demand Load Phase B: (A) | 13.8628
Connected Load Phase C: (A) |  |  | 13.8628 |  | 0 |  | 3840 | 0 | 0 | 0 |  | Demand Load Phase C: (A) | 13.8628
Total VA: | 9480
Load: (A) | 11.4079
25% Growth: (A) | 14.2599

## E1L-3N
Panel Schedule
Panel: E1L-3N | [16 empty] | Voltage (L-N): | 277
Voltage: 480Y/277 |  |  | Mains: MLO |  | Loads (VA) | [6 empty] | Loc: 3RD FL ELEC RM |  |  | AIC: 14K |  | Demand Factors:
Amps: 50 | Wires: 4 |  | Phase: 3 | [8 empty] | Mounting: SURFACE |  |  |  |  | Ltg: | 1.25
Branch Circuit | Amp | P | Description | Cir | Ltg |  | Recept |  | Motor | Lg Motor | Equip | Cir | Description | P | Amp | Branch Circuit | Recept(<10kVA): | 1
3/4" C/3#10+1#10GRD | 30 | 3 | XFMR T-7 | 1 | 480 | 1195 |  |  |  |  | 180 | 2 | LTG: TRIAGE, PDC RMS | 1 | 20 | 3/4" C/2#12+1#12GRD | Recept(>10kVA): | 0.5
- | - | - | - | 3 |  |  |  | 3840 |  |  | 180 | 4 | FIREMAN'S OUTLET | 2 | 20 | 3/4" C/2#12+1#12GRD | Motor: | 1
- | - | - | - | 5 | 480 |  |  | 3840 |  |  |  | 6 | - | - | - | - | Lg Motor: | 1.25
- | 20 | 1 | SPARE | 7 | [7 empty] | 8 | SPARE | 1 | 20 | - | Equip: | 1
- | 20 | 1 | SPARE | 9 | [7 empty] | 10 | SPARE | 1 | 20 | -
- | 20 | 1 | SPARE | 11 | [7 empty] | 12 | SPARE | 1 | 20 | -
- | - | 1 | SPACE | 13 | [7 empty] | 14 | SPACE | 1 | - | - | Recept Demand VA:
- | - | 1 | SPACE | 15 | [7 empty] | 16 | SPACE | 1 | - | - |  | Phase A | Phase B | Phase C | Total
- | - | 1 | SPACE | 17 | [7 empty] | 18 | SPACE | 1 | - | - | Total VA: | 0 | 3840 | 3840 | 7680
|  |  |  | 19 | [7 empty] | 20 |  |  |  |  | First 10kVA | 0 | 3840 | 3840 | 7680
|  |  |  | 21 | [7 empty] | 22 |  |  |  |  | Remaining VA: | 0 | 0 | 0 | 0
|  |  |  | 23 | [7 empty] | 24
|  |  |  | 25 | [7 empty] | 26
|  |  |  | 27 | [7 empty] | 28
|  |  |  | 29 | [7 empty] | 30
|  |  |  | 31 | [7 empty] | 32
|  |  |  | 33 | [7 empty] | 34
|  |  |  | 35 | [7 empty] | 36
|  |  |  | 37 | [7 empty] | 38
|  |  |  | 39 | [7 empty] | 40
|  |  |  | 41 | [7 empty] | 42
Connected Load Phase A: (A) |  |  | 6.6968 |  | 1675 |  | 0 |  | 0 | 0 | 180 |  | Demand Load Phase A: (A) | 8.2085
Connected Load Phase B: (A) |  |  | 14.5126 |  | 0 |  | 3840 |  | 0 | 0 | 180 |  | Demand Load Phase B: (A) | 14.5126
Connected Load Phase C: (A) |  |  | 15.5957 |  | 480 |  | 3840 |  | 0 | 0 | 0 |  | Demand Load Phase C: (A) | 16.0289
Total VA: | 10733.75
Load: (A) | 12.9167
25% Growth: (A) | 16.1458

## E1P-3N
Panel Schedule
Panel: E1P-3N | [14 empty] | Voltage (L-N): | 120
Voltage: 208Y/120 |  |  | Mains: MCB |  | Loads (VA) |  |  |  |  | Loc: 3RD FL ELEC RM |  |  | AIC: 10K |  | Demand Factors:
Amps: 50 | Wires: 4 |  | Phase: 3 | [6 empty] | Mounting: SURFACE |  |  |  |  | Ltg: | 1.25
Branch Circuit | Amp | P | Description | Cir | Ltg | Recept | Motor | Lg Motor | Equip | Cir | Description | P | Amp | Branch Circuit | Recept(<10kVA): | 1
3/4" C/2#12+1#12GRD | 20 | 1 | DOOR HOLD OPENS | 1 |  |  |  |  | 180 | 2 | SPARE | 1 | 20 | - | Recept(>10kVA): | 0.5
3/4" C/2#12+1#12GRD | 20 | 1 | DOOR HOLD OPENS: 4TH | 3 |  |  |  |  | 180 | 4 | SPARE | 1 | 20 | - | Motor: | 1
3/4" C/2#12+1#12GRD | 20 | 1 | LTG: ELEV CAB | 5 | 480 |  |  |  |  | 6 | SPARE | 1 | 20 | - | Lg Motor: | 1.25
3/4" C/2#12+1#12GRD | 20 | 1 | LTG: ELEV CAB | 7 | 480 |  |  |  |  | 8 | SPARE | 1 | 20 | - | Equip: | 1
- | 20 | 1 | SPARE | 9 | [5 empty] | 10 | SPARE | 1 | 20 | -
- | 20 | 1 | SPARE | 11 | [5 empty] | 12 | SPARE | 1 | 20 | -
- | - | 1 | SPACE | 13 | [5 empty] | 14 | SPACE | 1 | - | - | Recept Demand VA:
- | - | 1 | SPACE | 15 | [5 empty] | 16 | SPACE | 1 | - | - |  | Phase A | Phase B | Phase C | Total
- | - | 1 | SPACE | 17 | [5 empty] | 18 | SPACE | 1 | - | - | Total VA: | 0 | 0 | 0 | 0
|  |  |  | 19 | [5 empty] | 20 |  |  |  |  | First 10kVA | 0 | 0 | 0 | 0
|  |  |  | 21 | [5 empty] | 22 |  |  |  |  | Remaining VA: | 0 | 0 | 0 | 0
|  |  |  | 23 | [5 empty] | 24
|  |  |  | 25 | [5 empty] | 26
|  |  |  | 27 | [5 empty] | 28
|  |  |  | 29 | [5 empty] | 30
|  |  |  | 31 | [5 empty] | 32
|  |  |  | 33 | [5 empty] | 34
|  |  |  | 35 | [5 empty] | 36
|  |  |  | 37 | [5 empty] | 38
|  |  |  | 39 | [5 empty] | 40
|  |  |  | 41 | [5 empty] | 42
Connected Load Phase A: (A) |  |  | 5.5 |  | 480 | 0 | 0 | 0 | 180 |  | Demand Load Phase A: (A) | 6.5
Connected Load Phase B: (A) |  |  | 1.5 |  | 0 | 0 | 0 | 0 | 180 |  | Demand Load Phase B: (A) | 1.5
Connected Load Phase C: (A) |  |  | 4 |  | 480 | 0 | 0 | 0 | 0 |  | Demand Load Phase C: (A) | 5
Total VA: | 1560
Load: (A) | 4.3333
25% Growth: (A) | 5.4167

## E1L-4N
Panel Schedule
Panel: E1L-4N | [15 empty] | Voltage (L-N): | 277
Voltage: 480Y/277 |  |  | Mains: MLO |  | Loads (VA) | [5 empty] | Loc: 4TH FL ELEC RM |  |  | AIC: 14K |  | Demand Factors:
Amps: 50 | Wires: 4 |  | Phase: 3 | [7 empty] | Mounting: SURFACE |  |  |  |  | Ltg: | 1.25
Branch Circuit | Amp | P | Description | Cir | Ltg | Recept |  | Motor | Lg Motor | Equip | Cir | Description | P | Amp | Branch Circuit | Recept(<10kVA): | 1
3/4" C/2#12+1#12GRD | 20 | 1 | LTG: LOBBY, SHELL SPACE | 1 | 730 |  | 3840 |  |  |  | 2 | FIREMAN'S OUTLET | 2 | 20 | 3/4" C/2#12+1#12GRD | Recept(>10kVA): | 0.5
- | 20 | 1 | SPARE | 3 |  |  | 3840 |  |  |  | 4 | - | - | - | - | Motor: | 1
- | 20 | 1 | SPARE | 5 | [6 empty] | 6 | SPARE | 1 | 20 | - | Lg Motor: | 1.25
- | 20 | 1 | SPARE | 7 | [6 empty] | 8 | SPARE | 1 | 20 | - | Equip: | 1
- | 20 | 1 | SPARE | 9 | [6 empty] | 10 | SPARE | 1 | 20 | -
- | 20 | 1 | SPARE | 11 | [6 empty] | 12 | SPARE | 1 | 20 | -
- | - | 1 | SPACE | 13 | [6 empty] | 14 | SPACE | 1 | - | - | Recept Demand VA:
- | - | 1 | SPACE | 15 | [6 empty] | 16 | SPACE | 1 | - | - |  | Phase A | Phase B | Phase C | Total
- | - | 1 | SPACE | 17 | [6 empty] | 18 | SPACE | 1 | - | - | Total VA: | 3840 | 3840 | 0 | 7680
|  |  |  | 19 | [6 empty] | 20 |  |  |  |  | First 10kVA | 3840 | 3840 | 0 | 7680
|  |  |  | 21 | [6 empty] | 22 |  |  |  |  | Remaining VA: | 0 | 0 | 0 | 0
|  |  |  | 23 | [6 empty] | 24
|  |  |  | 25 | [6 empty] | 26
|  |  |  | 27 | [6 empty] | 28
|  |  |  | 29 | [6 empty] | 30
|  |  |  | 31 | [6 empty] | 32
|  |  |  | 33 | [6 empty] | 34
|  |  |  | 35 | [6 empty] | 36
|  |  |  | 37 | [6 empty] | 38
|  |  |  | 39 | [6 empty] | 40
|  |  |  | 41 | [6 empty] | 42
Connected Load Phase A: (A) |  |  | 16.4982 |  | 730 | 3840 |  | 0 | 0 | 0 |  | Demand Load Phase A: (A) | 17.157
Connected Load Phase B: (A) |  |  | 13.8628 |  | 0 | 3840 |  | 0 | 0 | 0 |  | Demand Load Phase B: (A) | 13.8628
Connected Load Phase C: (A) |  |  | 0 |  | 0 | 0 |  | 0 | 0 | 0 |  | Demand Load Phase C: (A) | 0
Total VA: | 8592.5
Load: (A) | 10.34
25% Growth: (A) | 12.9249

## E2L-2N
Panel Schedule
Panel: E2L-2N | [15 empty] | Voltage (L-N): | 277
Voltage: 480Y/277 |  |  | Mains: MLO |  | Loads (VA) | [5 empty] | Loc: 2ND FL ELEC RM |  |  | AIC: 14K |  | Demand Factors:
Amps: 50 | Wires: 4 |  | Phase: 3 | [7 empty] | Mounting: SURFACE |  |  |  |  | Ltg: | 1.25
Branch Circuit | Amp | P | Description | Cir | Ltg |  | Recept | Motor | Lg Motor | Equip | Cir | Description | P | Amp | Branch Circuit | Recept(<10kVA): | 1
3/" C/3#10+1#10GRD | 30 | 3 | XFMR T-6 | 1 | 1080 | 2378 | 2340 |  |  | 1080 | 2 | LTG: EXAM RMS, RM 208, 212 | 1 | 20 | 3/4" C/2#12+1#12GRD | Recept(>10kVA): | 0.5
- | - | - | - | 3 |  |  | 1080 |  |  | 2640 | 4 | SPARE | 1 | 20 | - | Motor: | 1
- | - | - | - | 5 |  |  | 1440 |  |  | 720 | 6 | SPARE | 1 | 20 | - | Lg Motor: | 1.25
- | 20 | 1 | SPARE | 7 | [6 empty] | 8 | SPARE | 1 | 20 | - | Equip: | 1
- | 20 | 1 | SPARE | 9 | [6 empty] | 10 | SPARE | 1 | 20 | -
- | 20 | 1 | SPARE | 11 | [6 empty] | 12 | SPARE | 1 | 20 | -
- | 20 | 1 | SPARE | 13 | [6 empty] | 14 | SPARE | 1 | 20 | - | Recept Demand VA:
- | - | 1 | SPACE | 15 | [6 empty] | 16 | SPACE | 1 | - | - |  | Phase A | Phase B | Phase C | Total
- | - | 1 | SPACE | 17 | [6 empty] | 18 | SPACE | 1 | - | - | Total VA: | 2340 | 1080 | 1440 | 4860
- | - | 1 | SPACE | 19 | [6 empty] | 20 | SPACE | 1 | - | - | First 10kVA | 2340 | 1080 | 1440 | 4860
- | - | 1 | SPACE | 21 | [6 empty] | 22 | SPACE | 1 | - | - | Remaining VA: | 0 | 0 | 0 | 0
- | - | 1 | SPACE | 23 | [6 empty] | 24 | SPACE | 1 | - | -
|  |  |  | 25 | [6 empty] | 26
|  |  |  | 27 | [6 empty] | 28
|  |  |  | 29 | [6 empty] | 30
|  |  |  | 31 | [6 empty] | 32
|  |  |  | 33 | [6 empty] | 34
|  |  |  | 35 | [6 empty] | 36
|  |  |  | 37 | [6 empty] | 38
|  |  |  | 39 | [6 empty] | 40
|  |  |  | 41 | [6 empty] | 42
Connected Load Phase A: (A) |  |  | 24.8303 |  | 3458 |  | 2340 | 0 | 0 | 1080 |  | Demand Load Phase A: (A) | 27.9513
Connected Load Phase B: (A) |  |  | 13.4296 |  | 0 |  | 1080 | 0 | 0 | 2640 |  | Demand Load Phase B: (A) | 13.4296
Connected Load Phase C: (A) |  |  | 7.7978 |  | 0 |  | 1440 | 0 | 0 | 720 |  | Demand Load Phase C: (A) | 7.7978
Total VA: | 13622.5
Load: (A) | 16.3929
25% Growth: (A) | 20.4911

## E2P-2N
Panel Schedule
Panel: E2P-2N | [17 empty] | Voltage (L-N): | 120
Voltage: 208Y/120 |  |  | Mains: MCB |  | Loads (VA) | [7 empty] | Loc: 2ND FL ELEC RM |  |  | AIC: 10K |  | Demand Factors:
Amps: 50 | Wires: 4 |  | Phase: 3 | [9 empty] | Mounting: SURFACE |  |  |  |  | Ltg: | 1.25
Branch Circuit | Amp | P | Description | Cir | Ltg |  | Recept |  | Motor | Lg Motor | Equip |  | Cir | Description | P | Amp | Branch Circuit | Recept(<10kVA): | 1
3/4" C/2#12+1#12GRD | 20 | 1 | REC: U/C REFRIG | 1 |  |  |  | 720 |  |  | 840 |  | 2 | HEADWALL UNITS 5 & 8 | 1 | 20 | 3/4" C/2#12+1#12GRD | Recept(>10kVA): | 0.5
3/4" C/2#12+1#12GRD | 20 | 1 | REC: U/C REFRIG | 3 |  |  |  | 720 |  |  | 840 |  | 4 | HEADWALL UNITS 6 & 7 | 1 | 20 | 3/4" C/2#12+1#12GRD | Motor: | 1
3/4" C/2#12+1#12GRD | 20 | 1 | REC: RM 2218 | 5 |  |  | 360 | 720 |  |  |  |  | 6 | HEADWALL UNITS 3 & 4 | 1 | 20 | 3/4" C/2#12+1#12GRD | Lg Motor: | 1.25
3/4" C/2#12+1#12GRD | 20 | 1 | REC: RM 2208 | 7 |  |  | 540 | 720 |  |  |  |  | 8 | HEADWALL UNITS 1 & 2 | 1 | 20 | 3/4" C/2#12+1#12GRD | Equip: | 1
3/4" C/2#12+1#12GRD | 20 | 1 | REC: ELECTRICAL RM | 9 |  |  | 360 |  |  |  |  | 1200 | 10 | NURSE CALL CTRL PANEL | 1 | 20 | 3/4" C/2#12+1#12GRD
3/4" C/2#12+1#12GRD | 20 | 1 | REC: RM 2226 | 11 |  |  | 360 |  |  |  |  | 600 | 12 | DDC: CONTROL PANEL | 1 | 20 | 3/4" C/2#12+1#12GRD
- | 20 | 1 | SPARE | 13 |  | 1080 |  | 360 |  |  |  |  | 14 | AHU-2N LTS & REC | 1 | 20 | 3/4" C/2#12+1#12GRD | Recept Demand VA:
- | 20 | 1 | SPARE | 15 | [7 empty] | 600 | 16 | DDC: CONTROL PANEL | 1 | 20 | 3/4" C/2#12+1#12GRD |  | Phase A | Phase B | Phase C | Total
- | 20 | 1 | SPARE | 17 | [7 empty] | 120 | 18 | ELEVATOR SHUNT TRIP | 1 | 20 | 3/4" C/2#12+1#12GRD | Total VA: | 2340 | 1080 | 1440 | 4860
- | 20 | 1 | SPARE | 19 | [7 empty] | 240 | 20 | SECURITY CAMERA | 1 | 20 | 3/4" C/2#12+1#12GRD | First 10kVA | 2340 | 1080 | 1440 | 4860
- | 20 | 1 | SPARE | 21 | [8 empty] | 22 | SPARE | 1 | 20 | - | Remaining VA: | 0 | 0 | 0 | 0
- | 20 | 1 | SPARE | 23 | [8 empty] | 24 | SPARE | 1 | 20 | -
- | 20 | 1 | SPARE | 25 | [8 empty] | 26 | SPARE | 1 | 20 | -
- | 20 | 1 | SPARE | 27 | [8 empty] | 28 | SPARE | 1 | 20 | -
- | 20 | 1 | SPARE | 29 | [8 empty] | 30 | SPARE | 1 | 20 | -
- | 20 | 1 | SPARE | 31 | [8 empty] | 32 | SPARE | 1 | 20 | -
- | 20 | 1 | SPARE | 33 | [8 empty] | 34 | SPARE | 1 | 20 | -
- | 20 | 1 | SPARE | 35 | [8 empty] | 36 | SPARE | 1 | 20 | -
- | - | 1 | SPACE | 37 | [8 empty] | 38 | SPACE | 1 | - | -
- | - | 1 | SPACE | 39 | [8 empty] | 40 | SPACE | 1 | - | -
- | - | 1 | SPACE | 41 | [8 empty] | 42 | SPACE | 1 | - | -
Connected Load Phase A: (A) |  |  | 37.5 |  | 1080 |  | 2340 |  | 0 | 0 | 1080 |  |  | Demand Load Phase A: (A) | 39.75
Connected Load Phase B: (A) |  |  | 31 |  | 0 |  | 1080 |  | 0 | 0 | 2640 |  |  | Demand Load Phase B: (A) | 31
Connected Load Phase C: (A) |  |  | 18 |  | 0 |  | 1440 |  | 0 | 0 | 720 |  |  | Demand Load Phase C: (A) | 18
Total VA: | 10650
Load: (A) | 29.5833
25% Growth: (A) | 36.9792

## E2L-3N
Panel Schedule
Panel: E2L-3N | [17 empty] | Voltage (L-N): | 277
Voltage: 480Y/277 |  |  | Mains: MLO |  | Loads (VA) | [7 empty] | Loc: 3RD FL ELEC RM |  |  | AIC: 14K |  | Demand Factors:
Amps: 100 | Wires: 4 |  | Phase: 3 | [9 empty] | Mounting: SURFACE |  |  |  |  | Ltg: | 1.25
Branch Circuit | Amp | P | Description | Cir | Ltg |  | Recept |  | Motor | Lg Motor | Equip |  | Cir | Description | P | Amp | Branch Circuit | Recept(<10kVA): | 1
3/4" C/3#8+1#10GRD | 45 | 3 | XFMR T-8 | 1 |  | 3458 | 3780 | 2340 |  |  | 5640 | 1080 | 2 | PANEL E2L-2N | 3 | 50 | 3/4" C/4#8+1#10GRD | Recept(>10kVA): | 0.5
- | - | - | - | 3 |  |  | 2700 | 1080 |  |  | 4680 | 2640 | 4 | - | - | - | - | Motor: | 1
- | - | - | - | 5 |  |  | 3960 | 1440 |  |  | 3600 | 720 | 6 | - | - | - | - | Lg Motor: | 1.25
3/4" C/2#12+1#12GRD | 20 | 1 | LTG: TRIAGE, PDC RMS | 7 | 1190 | [7 empty] | 8 | SPARE | 1 | 20 | - | Equip: | 1
3/4" C/2#12+1#12GRD | 20 | 1 | LTG: TESTING, NURSE ST | 9 | 1910 | [7 empty] | 10 | SPARE | 1 | 20 | -
- | 20 | 1 | SPARE | 11 | [8 empty] | 12 | SPARE | 1 | 20 | -
- | 20 | 1 | SPARE | 13 | [8 empty] | 14 | SPARE | 1 | 20 | - | Recept Demand VA:
- | 20 | 1 | SPARE | 15 | [8 empty] | 16 | SPARE | 1 | 20 | - |  | Phase A | Phase B | Phase C | Total
- | 20 | 1 | SPARE | 17 | [8 empty] | 18 | SPARE | 1 | 20 | - | Total VA: | 6120 | 3780 | 5400 | 15300
- | - | 1 | SPACE | 19 | [8 empty] | 20 | SPACE | 1 | - | - | First 10kVA | 6120 | 3780 | 5400 | 10000
- | - | 1 | SPACE | 21 | [8 empty] | 22 | SPACE | 1 | - | - | Remaining VA: | 0 | 0 | 0 | 5300
- | - | 1 | SPACE | 23 | [8 empty] | 24 | SPACE | 1 | - | -
|  |  |  | 25 | [8 empty] | 26
|  |  |  | 27 | [8 empty] | 28
|  |  |  | 29 | [8 empty] | 30
|  |  |  | 31 | [8 empty] | 32
|  |  |  | 33 | [8 empty] | 34
|  |  |  | 35 | [8 empty] | 36
|  |  |  | 37 | [8 empty] | 38
|  |  |  | 39 | [8 empty] | 40
|  |  |  | 41 | [8 empty] | 42
Connected Load Phase A: (A) |  |  | 63.1336 |  | 4648 |  | 6120 |  | 0 | 0 | 6720 |  |  | Demand Load Phase A: (A) | 67.3285
Connected Load Phase B: (A) |  |  | 46.9675 |  | 1910 |  | 3780 |  | 0 | 0 | 7320 |  |  | Demand Load Phase B: (A) | 48.6913
Connected Load Phase C: (A) |  |  | 35.0903 |  | 0 |  | 5400 |  | 0 | 0 | 4320 |  |  | Demand Load Phase C: (A) | 35.0903
Total VA: | 39207.5
Load: (A) | 47.1811
25% Growth: (A) | 58.9764

## E2P-3N
Panel Schedule
Panel: E2P-3N | [16 empty] | Voltage (L-N): | 120
Voltage: 208Y/120 |  |  | Mains: MCB |  | Loads (VA) | [6 empty] | Loc: 3RD FL ELEC RM |  |  | AIC: 10K |  | Demand Factors:
Amps: 100 | Wires: 4 |  | Phase: 3 | [8 empty] | Mounting: SURFACE |  |  |  |  | Ltg: | 1.25
Branch Circuit | Amp | P | Description | Cir | Ltg | Recept |  | Motor | Lg Motor | Equip |  | Cir | Description | P | Amp | Branch Circuit | Recept(<10kVA): | 1
3/4" C/2#12+1#12GRD | 20 | 1 | REC: RM 3200 | 1 |  | 540 | 720 |  |  |  |  | 2 | HEADWALL UNITS: ANTEP. | 1 | 20 | 3/4" C/2#12+1#12GRD | Recept(>10kVA): | 0.5
3/4" C/2#12+1#12GRD | 20 | 1 | REC: RM 3204 | 3 |  | 540 | 540 |  |  |  |  | 4 | REC: RMS 3211, 3213 | 1 | 20 | 3/4" C/2#12+1#12GRD | Motor: | 1
3/4" C/2#12+1#12GRD | 20 | 1 | REC: RM 3208 | 5 |  | 180 | 1080 |  |  | 600 |  | 6 | HEADWALL UNITS: ULTRAS. | 1 | 20 | 3/4" C/2#12+1#12GRD | Lg Motor: | 1.25
3/4" C/2#12+1#12GRD | 20 | 1 | REC: FETAL MONITORS | 7 | [5 empty] | 1200 | 840 | 8 | REC: SPECIMEN REFRIG | 1 | 20 | 3/4" C/2#12+1#12GRD | Equip: | 1
3/4" C/2#12+1#12GRD | 20 | 1 | REC: FETAL MONITORS | 9 | [5 empty] | 1200 | 1440 | 10 | REC: STERILIZER | 1 | 20 | 3/4" C/2#12+1#12GRD
3/4" C/2#12+1#12GRD | 20 | 1 | REC: RMS 3215, 3219 | 11 |  | 360 |  |  |  |  | 1200 | 12 | REC: MICROSCOPE | 1 | 20 | 3/4" C/2#12+1#12GRD
3/4" C/2#12+1#12GRD | 20 | 1 | REC: FETAL MONITORS | 13 |  |  | 900 |  |  | 1800 |  | 14 | REC: TRIAGE RMS 4, 5, 6 | 1 | 20 | 3/4" C/2#12+1#12GRD | Recept Demand VA:
3/4" C/2#12+1#12GRD | 20 | 1 | REC: FETAL MONITORS | 15 |  |  | 900 |  |  | 1200 |  | 16 | REC: TRIAGE RMS 6, 7, 8 | 1 | 20 | 3/4" C/2#12+1#12GRD |  | Phase A | Phase B | Phase C | Total
3/4" C/2#12+1#12GRD | 20 | 1 | REC: TRIAGE RMS 1, 2, 3 | 17 |  | 1080 |  |  |  |  | 1800 | 18 | REC: FETAL MONITORS | 1 | 20 | 3/4" C/2#12+1#12GRD | Total VA: | 3780 | 2700 | 3960 | 10440
3/4" C/2#12+1#12GRD | 20 | 1 | HEADWALL UNITS: TRIAGE | 19 |  | 720 | 180 |  |  |  | 600 | 20 | REC: MONITORS RM 3231 | 1 | 20 | 3/4" C/2#12+1#12GRD | First 10kVA | 3780 | 2700 | 3960 | 10000
3/4" C/2#12+1#12GRD | 20 | 1 | HEADWALL UNITS: TRIAGE | 21 |  | 720 |  |  |  |  | 240 | 22 | REC: CRASH CART | 1 | 20 | 3/4" C/2#12+1#12GRD | Remaining VA: | 0 | 0 | 0 | 440
3/4" C/2#12+1#12GRD | 20 | 1 | HEADWALL UNITS: TRIAGE | 23 |  | 720 | 540 |  |  |  |  | 24 | REC: ELECTRICAL RM | 1 | 20 | 3/4" C/2#12+1#12GRD
3/4" C/2#12+1#12GRD | 20 | 1 | HEADWALL UNITS: TRIAGE | 25 |  | 720 |  |  |  |  | 1200 | 26 | NURSE CALL CTRL PANEL | 1 | 20 | 3/4" C/2#12+1#12GRD
3/4" C/2#12+1#12GRD | 20 | 1 | REC: COUNTERTOP FRIG | 27 | [5 empty] | 600 |  | 28 | SPARE | 1 | 20 | -
- | 20 | 1 | SPARE | 29 | [7 empty] | 30 | SPARE | 1 | 20 | -
- | 20 | 1 | SPARE | 31 | [7 empty] | 32 | SPARE | 1 | 20 | -
- | 20 | 1 | SPARE | 33 | [7 empty] | 34 | SPARE | 1 | 20 | -
- | 20 | 1 | SPARE | 35 | [7 empty] | 36 | SPARE | 1 | 20 | -
- | - | 1 | SPACE | 37 | [7 empty] | 38 | SPACE | 1 | - | -
- | - | 1 | SPACE | 39 | [7 empty] | 40 | SPACE | 1 | - | -
- | - | 1 | SPACE | 41 | [7 empty] | 42 | SPACE | 1 | - | -
Connected Load Phase A: (A) |  |  | 78.5 |  | 0 | 3780 |  | 0 | 0 | 5640 |  |  | Demand Load Phase A: (A) | 78.5
Connected Load Phase B: (A) |  |  | 61.5 |  | 0 | 2700 |  | 0 | 0 | 4680 |  |  | Demand Load Phase B: (A) | 61.5
Connected Load Phase C: (A) |  |  | 63 |  | 0 | 3960 |  | 0 | 0 | 3600 |  |  | Demand Load Phase C: (A) | 63
Total VA: | 24140
Load: (A) | 67.0556
25% Growth: (A) | 83.8194

## E3L-N
Panel Schedule
Panel: E3L-N | [16 empty] | Voltage (L-N): | 277
Voltage: 480Y/277 |  |  | Mains: MLO |  | Loads (VA) | [6 empty] | Loc: 2ND FL ELEC RM |  |  | AIC: 25K |  | Demand Factors:
Amps: 250 | Wires: 4 |  | Phase: 3 | [8 empty] | Mounting: SURFACE |  |  |  |  | Ltg: | 1.25
Branch Circuit | Amp | P | Description | Cir | Ltg | Recept | Motor |  | Lg Motor | Equip |  | Cir | Description | P | Amp | Branch Circuit | Recept(<10kVA): | 1
1 1/4" C/3#1+1#6GRD | 200 | 3 | AHU-2N SUPPLY FAN | 1 |  |  |  |  | 18642 |  |  | 2 | 200AF PREPARED SPACE | 3 | - | - | Recept(>10kVA): | 0.5
- | - | - | - | 3 |  |  |  |  | 18642 |  |  | 4 | - | - | - | - | Motor: | 1
- | - | - | - | 5 |  |  |  |  | 18642 |  |  | 6 | - | - | - | - | Lg Motor: | 1.25
3/4" C/3#10+1#10GRD | 25 | 3 | SECOND. PUMP P-HS-1 | 7 |  |  | 1864 |  |  |  | 6097 | 8 | DUPLEX CONDEN. RECV'R | 3 | 40 | 3/4" C/3#10+1#10GRD | Equip: | 1
- | - | - | - | 9 |  |  | 1864 |  |  |  | 6097 | 10 | - | - | - | -
- | - | - | - | 11 |  |  | 1864 |  |  |  | 6097 | 12 | - | - | - | -
3/4" C/3#10+1#10GRD | 45 | 3 | SMOKE PRESS. FAN SF-1 | 13 |  |  | 3728 | 3048 |  |  |  | 14 | ACCU-1: 1ST FLOOR ROOF | 3 | 20 | 3/4" C/3#12+1#12GRD | Recept Demand VA:
- | - | - | - | 15 |  |  | 3728 | 3048 |  |  |  | 16 | - | - | - | - |  | Phase A | Phase B | Phase C | Total
- | - | - | - | 17 |  |  | 3728 | 3048 |  |  |  | 18 | - | - | - | - | Total VA: | 0 | 360 | 0 | 360
- | - | 3 | 100AF PREPARED SPACE | 19 | [7 empty] | 20 | 100AF PREPARED SPACE | 3 | - | - | First 10kVA | 0 | 360 | 0 | 360
- | - | - | - | 21 | [7 empty] | 22 | - | - | - | - | Remaining VA: | 0 | 0 | 0 | 0
- | - | - | - | 23 | [7 empty] | 24 | - | - | - | -
3/4" C/3#6+1#8GRD | 30 | 3 | XFMR T-10 | 25 |  |  | 6282 |  |  | 720 |  | 26 | SPACE | 1 | - | -
- | - | - | - | 27 | 1080 | 360 | 6096 |  |  | 720 |  | 28 | SPACE | 1 | - | -
- | - | - | - | 29 |  |  | 6096 |  |  | 720 |  | 30 | SPACE | 1 | - | -
- | - | 1 | SPACE | 31 | [7 empty] | 32 | SPACE | 1 | - | -
- | - | 1 | SPACE | 33 | [7 empty] | 34 | SPACE | 1 | - | -
- | - | 1 | SPACE | 35 | [7 empty] | 36 | SPACE | 1 | - | -
- | - | 1 | SPACE | 37 | [7 empty] | 38 | SPACE | 1 | - | -
- | - | 1 | SPACE | 39 | [7 empty] | 40 | SPACE | 1 | - | -
- | - | 1 | SPACE | 41 | [7 empty] | 42 | SPACE | 1 | - | -
Connected Load Phase A: (A) |  |  | 145.7798 |  | 0 | 0 | 14922 |  | 18642 | 6817 |  |  | Demand Load Phase A: (A) | 162.6047
Connected Load Phase B: (A) |  |  | 150.3069 |  | 1080 | 360 | 14736 |  | 18642 | 6817 |  |  | Demand Load Phase B: (A) | 168.1065
Connected Load Phase C: (A) |  |  | 145.1083 |  | 0 | 0 | 14736 |  | 18642 | 6817 |  |  | Demand Load Phase C: (A) | 161.9332
Total VA: | 136462.5
Load: (A) | 164.2148
25% Growth: (A) | 205.2685

## E3P-N
Panel Schedule
Panel: E3P-N | [19 empty] | Voltage (L-N): | 120
Voltage: 208Y/120 |  |  | Mains: MCB |  | Loads (VA) | [9 empty] | Loc: 2ND FL ELEC RM |  |  | AIC: 10K |  | Demand Factors:
Amps: 100 | Wires: 4 |  | Phase: 3 | [11 empty] | Mounting: SURFACE |  |  |  |  | Ltg: | 1.25
Branch Circuit | Amp | P | Description | Cir | Ltg |  | Recept |  | Motor |  | Lg Motor |  | Equip |  | Cir | Description | P | Amp | Branch Circuit | Recept(<10kVA): | 1
3/4" C/2#12+1#12GRD | 20 | 1 | ELEVATOR SHUNT TRIP | 1 | [8 empty] | 120 | 600 | 2 | DDC: CONTROL PANEL | 1 | 20 | 3/4" C/2#12+1#12GRD | Recept(>10kVA): | 0.5
3/4" C/2#12+1#12GRD | 20 | 1 | ACU-1 | 3 |  | 1080 |  | 360 |  |  |  |  | 120 |  | 4 | AHU-2N LTS & REC | 1 | 20 | 3/4" C/2#12+1#12GRD | Motor: | 1
3/4" C/2#12+1#12GRD | 20 | 1 | ACU-1 | 5 | [8 empty] | 120 | 600 | 6 | DDC: CONTROL PANEL | 1 | 20 | 3/4" C/2#12+1#12GRD | Lg Motor: | 1.25
3/4" C/2#12+1#12GRD | 20 | 1 | REC: ELEV MACHINE RM | 7 | [5 empty] | 186 |  |  |  |  | 8 | AHU-2N PREHEAT PUMP | 1 | 15 | 3/4" C/2#12+1#12GRD | Equip: | 1
3/4" C/3#10+1#10GRD | 30 | 3 | ACCU-1 | 9 |  |  |  |  | 3048 |  |  |  |  | 600 | 10 | SMOKE FAN DAMPER | 1 | 20 | 3/4" C/2#12+1#12GRD
- | - | - | - | 11 |  |  |  |  | 3048 |  |  | 3048 |  |  | 12 | ACCU-1 | 3 | 30 | 3/4" C/3#10+1#10GRD
- | - | - | - | 13 |  |  |  |  | 3048 |  |  | 3048 |  |  | 14 | - | - | - | - | Recept Demand VA:
- | 20 | 1 | SPARE | 15 | [7 empty] | 3048 |  |  | 16 | - | - | - | - |  | Phase A | Phase B | Phase C | Total
- | 20 | 1 | SPARE | 17 | [10 empty] | 18 | SPARE | 1 | 20 | - | Total VA: | 0 | 360 | 0 | 360
- | 20 | 1 | SPARE | 19 | [10 empty] | 20 | SPARE | 1 | 20 | - | First 10kVA | 0 | 360 | 0 | 360
- | 20 | 1 | SPARE | 21 | [10 empty] | 22 | SPARE | 1 | 20 | - | Remaining VA: | 0 | 0 | 0 | 0
- | 20 | 1 | SPARE | 23 | [10 empty] | 24 | SPARE | 1 | 20 | -
- | - | 1 | SPACE | 25 | [10 empty] | 26 | SPACE | 1 | - | -
- | - | 1 | SPACE | 27 | [10 empty] | 28 | SPACE | 1 | - | -
- | - | 1 | SPACE | 29 | [10 empty] | 30 | SPACE | 1 | - | -
- | - | 1 | SPACE | 31 | [10 empty] | 32 | SPACE | 1 | - | -
- | - | 1 | SPACE | 33 | [10 empty] | 34 | SPACE | 1 | - | -
- | - | 1 | SPACE | 35 | [10 empty] | 36 | SPACE | 1 | - | -
- | - | 1 | SPACE | 37 | [10 empty] | 38 | SPACE | 1 | - | -
- | - | 1 | SPACE | 39 | [10 empty] | 40 | SPACE | 1 | - | -
- | - | 1 | SPACE | 41 | [10 empty] | 42 | SPACE | 1 | - | -
Connected Load Phase A: (A) |  |  | 58.35 |  | 0 |  | 0 |  | 3234 |  | 3048 |  | 720 |  |  | Demand Load Phase A: (A) | 64.7
Connected Load Phase B: (A) |  |  | 68.8 |  | 1080 |  | 360 |  | 3048 |  | 3048 |  | 720 |  |  | Demand Load Phase B: (A) | 77.4
Connected Load Phase C: (A) |  |  | 56.8 |  | 0 |  | 0 |  | 3048 |  | 3048 |  | 720 |  |  | Demand Load Phase C: (A) | 63.15
Total VA: | 24630
Load: (A) | 68.4167
25% Growth: (A) | 85.5208

## E6L-N-ELEV
Panel Schedule
Panel: E6L-N-ELEV | [15 empty] | Voltage (L-N): | 277
Voltage: 480 |  |  | Mains: MLO |  | Loads (VA) | [5 empty] | Loc: ELEV MACH RM |  |  | AIC: 35K |  | Demand Factors:
Amps: 225 | Wires: 3 |  | Phase: 3 | [7 empty] | Mounting: SURFACE |  |  |  |  | Ltg: | 1.25
Branch Circuit | Amp | P | Description | Cir | Ltg | Recept | Motor | Lg Motor |  | Equip | Cir | Description | P | Amp | Branch Circuit | Recept(<10kVA): | 1
3/4" C/3#6+1#10GRD | 60 | 3 | ELEVATOR #1 | 1 |  |  | 4971 |  | 4971 |  | 2 | ELEVATOR #2 | 3 | 60 | 3/4" C/3#6+1#10GRD | Recept(>10kVA): | 0.5
- | - | - | - | 3 |  |  | 4971 |  | 4971 |  | 4 | - | - | - | - | Motor: | 1
- | - | - | - | 5 |  |  | 4971 |  | 4971 |  | 6 | - | - | - | - | Lg Motor: | 1.25
- | - | 1 | SPACE | 7 | [6 empty] | 8 | SPACE | 1 | - | - | Equip: | 1
- | - | 1 | SPACE | 9 | [6 empty] | 10 | SPACE | 1 | - | -
- | - | 1 | SPACE | 11 | [6 empty] | 12 | SPACE | 1 | - | -
|  |  |  | 13 | [6 empty] | 14 |  |  |  |  | Recept Demand VA:
|  |  |  | 15 | [6 empty] | 16 | [5 empty] | Phase A | Phase B | Phase C | Total
|  |  |  | 17 | [6 empty] | 18 |  |  |  |  | Total VA: | 0 | 0 | 0 | 0
|  |  |  | 19 | [6 empty] | 20 |  |  |  |  | First 10kVA | 0 | 0 | 0 | 0
|  |  |  | 21 | [6 empty] | 22 |  |  |  |  | Remaining VA: | 0 | 0 | 0 | 0
|  |  |  | 23 | [6 empty] | 24
|  |  |  | 25 | [6 empty] | 26
|  |  |  | 27 | [6 empty] | 28
|  |  |  | 29 | [6 empty] | 30
|  |  |  | 31 | [6 empty] | 32
|  |  |  | 33 | [6 empty] | 34
|  |  |  | 35 | [6 empty] | 36
|  |  |  | 37 | [6 empty] | 38
|  |  |  | 39 | [6 empty] | 40
|  |  |  | 41 | [6 empty] | 42
Connected Load Phase A: (A) |  |  | 35.8917 |  | 0 | 0 | 4971 | 4971 |  | 0 |  | Demand Load Phase A: (A) | 40.3782
Connected Load Phase B: (A) |  |  | 35.8917 |  | 0 | 0 | 4971 | 4971 |  | 0 |  | Demand Load Phase B: (A) | 40.3782
Connected Load Phase C: (A) |  |  | 35.8917 |  | 0 | 0 | 4971 | 4971 |  | 0 |  | Demand Load Phase C: (A) | 40.3782
Total VA: | 33554.25
Load: (A) | 40.3782
25% Growth: (A) | 50.4727

## ME1L-N
Panel Schedule
Panel: ME1L-N | [16 empty] | Voltage (L-N): | 277
Voltage: 480Y/277 |  |  | Mains: MLO |  | Loads (VA) | [6 empty] | Loc: 2ND FL ELEC RM |  |  | AIC: 25K |  | Demand Factors:
Amps: 100 | Wires: 4 |  | Phase: 3 | [8 empty] | Mounting: SURFACE |  |  |  |  | Ltg: | 1.25
Branch Circuit | Amp | P | Description | Cir | Ltg |  | Recept |  | Motor | Lg Motor | Equip | Cir | Description | P | Amp | Branch Circuit | Recept(<10kVA): | 1
3/4" C/4#8+1#10GRD | 50 | 3 | PANEL E1L-1N | 1 | 4071 | 1440 | 360 |  |  |  | 4210 | 2 | PANEL E1L-2N | 3 | 50 | 3/4" C/4#8+1#10GRD | Recept(>10kVA): | 0.5
- | - | - | - | 3 | 1278 |  |  | 3840 |  |  | 1920 | 4 | - | - | - | - | Motor: | 1
- | - | - | - | 5 | 1272 |  |  | 3840 |  |  | 2580 | 6 | - | - | - | - | Lg Motor: | 1.25
3/4" C/4#8+1#10GRD | 50 | 3 | PANEL E1L-3N | 7 | 1675 | 730 |  | 3840 |  |  | 180 | 8 | PANEL E1L-4N | 3 | 50 | 3/4" C/4#8+1#10GRD | Equip: | 1
- | - | - | - | 9 |  |  | 3840 | 3840 |  |  | 180 | 10 | - | - | - | -
- | - | - | - | 11 | 480 |  | 3840 |  |  |  |  | 12 | - | - | - | -
- | - | 3 | SPACE | 13 | [7 empty] | 14 | SPACE | 3 | - | - | Recept Demand VA:
- | - | - | - | 15 | [7 empty] | 16 | - | - | - | - |  | Phase A | Phase B | Phase C | Total
- | - | - | - | 17 | [7 empty] | 18 | - | - | - | - | Total VA: | 4200 | 11520 | 7680 | 23400
- | - | 3 | SPACE | 19 | [7 empty] | 20 | SPACE | 3 | - | - | First 10kVA | 4200 | 10000 | 7680 | 10000
- | - | - | - | 21 | [7 empty] | 22 | - | - | - | - | Remaining VA: | 0 | 1520 | 0 | 13400
- | - | - | - | 23 | [7 empty] | 24 | - | - | - | -
|  |  |  | 25 | [7 empty] | 26
|  |  |  | 27 | [7 empty] | 28
|  |  |  | 29 | [7 empty] | 30
|  |  |  | 31 | [7 empty] | 32
|  |  |  | 33 | [7 empty] | 34
|  |  |  | 35 | [7 empty] | 36
|  |  |  | 37 | [7 empty] | 38
|  |  |  | 39 | [7 empty] | 40
|  |  |  | 41 | [7 empty] | 42
Connected Load Phase A: (A) |  |  | 59.5884 |  | 7916 |  | 4200 |  | 0 | 0 | 4390 |  | Demand Load Phase A: (A) | 66.7329
Connected Load Phase B: (A) |  |  | 53.7834 |  | 1278 |  | 11520 |  | 0 | 0 | 2100 |  | Demand Load Phase B: (A) | 52.1931
Connected Load Phase C: (A) |  |  | 43.3646 |  | 1752 |  | 7680 |  | 0 | 0 | 2580 |  | Demand Load Phase C: (A) | 44.9458
Total VA: | 39452.5
Load: (A) | 47.4759
25% Growth: (A) | 59.3449