## Slide 1
Northeastern Illinois University’s El Centro Building
Chicago, Illinois
Michael Gramarossa, BAE/MAE
Mechanical Option
Advisor: Dr. James Freihaut
JGMA
JGMA

## Slide 2
Building Summary
Thesis Objective
Mechanical Depth
Structural Breadth
Electrical Breadth
Evaluation and Conclusion
JGMA
JGMA

## Slide 3
Michael Gramarossa Northeastern Illinois University’s El Centro Mechanical Option
Building Summary
  Overview
  Existing Mechanical System
    Cooling and Ventilation
    Heating
Thesis Objective
Mechanical Depth
Structural Breadth
Electrical Breadth
Evaluation & Conclusion
Site and Location
Chicago Illinois
  Summer: 91.9°F (0.4%)
  Winter -4.0°F (99.6%)

## Slide 4
Michael Gramarossa Northeastern Illinois University’s El Centro Mechanical Option
Site and Location
Chicago Illinois
  Summer: 91.9°F (0.4%)
  Winter -4.0°F (99.6%)
Located along Kennedy Expressway
Building Summary
  Overview
  Existing Mechanical System
    Cooling and Ventilation
    Heating
Thesis Objective
Mechanical Depth
Structural Breadth
Electrical Breadth
Evaluation & Conclusion

## Slide 5
Michael Gramarossa Northeastern Illinois University’s El Centro Mechanical Option
archpaper.com
Site and Location
Chicago Illinois
  Summer: 91.9°F (0.4%)
  Winter -4.0°F (99.6%)
Located along Kennedy Expressway
Passed by 400,000 vehicles each day
Building Summary
  Overview
  Existing Mechanical System
    Cooling and Ventilation
    Heating
Thesis Objective
Mechanical Depth
Structural Breadth
Electrical Breadth
Evaluation & Conclusion

## Slide 6
Michael Gramarossa Northeastern Illinois University’s El Centro Mechanical Option
Recently completed in September 2014
3 stories (no basement)
55,000 ft2
Classrooms, offices, labs, lounges, etc.
Architecture and Façade
Building Summary
  Overview
  Existing Mechanical System
    Cooling and Ventilation
    Heating
Thesis Objective
Mechanical Depth
Structural Breadth
Electrical Breadth
Evaluation & Conclusion
JGMA

## Slide 7
Michael Gramarossa Northeastern Illinois University’s El Centro Mechanical Option
Architecture and Façade
Recently completed in September 2014
3 stories (no basement)
55,000 ft2
Classrooms, offices, labs, lounges, etc.
Curtain Wall Façade with solar fins
Blue and Gold Fins
Building Summary
  Overview
  Existing Mechanical System
    Cooling and Ventilation
    Heating
Thesis Objective
Mechanical Depth
Structural Breadth
Electrical Breadth
Evaluation & Conclusion
JGMA
JGMA
Chicagoarchitectue.com

## Slide 8
Michael Gramarossa Northeastern Illinois University’s El Centro Mechanical Option
[2] 100 ton air handling roof top units (RTUs)
The RTUs supply 55°F air year round
Existing Mechanical System
Cooling and Ventilation
Building Summary
  Overview
  Existing Mechanical System
    Cooling and Ventilation
    Heating
Thesis Objective
Mechanical Depth
Structural Breadth
Electrical Breadth
Evaluation & Conclusion
JGMA

## Slide 9
Michael Gramarossa Northeastern Illinois University’s El Centro Mechanical Option
Unit | Area Served (ft2) | Supply Capacity (CFM) | Ventilation (CFM) | Cooling (Ton) | Heating (MBh)
RTU-1 | 24,000 | 38,000 | 12,000 | 100 | 1250
RTU-2 | 27,800 | 38,000 | 12,000 | 100 | 1250
Existing Mechanical System
Cooling and Ventilation
[2] 100 ton air handling roof top units (RTUs)
The RTUs supply 55°F air year round
RTU-1 & RTU-2
Separate Air Cooled Condensing Units (CU-1 & CU-2)
Building Summary
  Overview
  Existing Mechanical System
    Cooling and Ventilation
    Heating
Thesis Objective
Mechanical Depth
Structural Breadth
Electrical Breadth
Evaluation & Conclusion
JGMA

## Slide 10
Michael Gramarossa Northeastern Illinois University’s El Centro Mechanical Option
Existing Mechanical System
Heating
Tag | Fuel Type | Rating (MBH) |  | Water Temperature (°F) |  | Flow Rate (GPM) | Min. Thermal Efficiency (%)
 |  | Input | Output | Entering | Leaving |  | 
B-1 | NG | 750 | 657 | 130 | 150 | 66 | 90
B-2 | NG | 750 | 657 | 130 | 150 | 66 | 90
[2] 750 MBh Boilers
Boilers serve 71 VAV reheat coils and hot water radiant finned tubes
Building Summary
  Overview
  Existing Mechanical System
    Cooling and Ventilation
    Heating
Thesis Objective
Mechanical Depth
Structural Breadth
Electrical Breadth
Evaluation & Conclusion

## Slide 11
Michael Gramarossa Northeastern Illinois University’s El Centro Mechanical Option
Existing Mechanical System
Heating
Second Floor Plan Hot Water Schematic
Tag | Fuel Type | Rating (MBH) |  | Water Temperature (°F) |  | Flow Rate (GPM) | Min. Thermal Efficiency (%)
 |  | Input | Output | Entering | Leaving |  | 
B-1 | NG | 750 | 657 | 130 | 150 | 66 | 90
B-2 | NG | 750 | 657 | 130 | 150 | 66 | 90
[2] 750 MBh Boilers
Boilers serve 71 VAV reheat coils and hot water radiant finned tubes
Building Summary
  Overview
  Existing Mechanical System
    Cooling and Ventilation
    Heating
Thesis Objective
Mechanical Depth
Structural Breadth
Electrical Breadth
Evaluation & Conclusion

## Slide 12
Michael Gramarossa Northeastern Illinois University’s El Centro Mechanical Option
The Chicago Building Code (CBC) requires a certain amount of airflow be supplied to a space regardless of the load
Building Summary
Thesis Objective
Mechanical Depth
Structural Breadth
Electrical Breadth
Evaluation and Conclusion
Thesis Objective

## Slide 13
Michael Gramarossa Northeastern Illinois University’s El Centro Mechanical Option
The Chicago Building Code (CBC) requires a certain amount of airflow be supplied to a space regardless of the load
Redesign the current mechanical system according to the International Building Code (IBC)
Thesis Objective
Building Summary
Thesis Objective
Mechanical Depth
Structural Breadth
Electrical Breadth
Evaluation and Conclusion

## Slide 14
Michael Gramarossa Northeastern Illinois University’s El Centro Mechanical Option
Thesis Objective
The Chicago Building Code (CBC) requires a certain amount of airflow be supplied to a space regardless of the load
Redesign the current mechanical system according to the International Building Code (IBC)
What are the greater implications if all mechanical systems for commercial buildings in Chicago were designed to the IBC rather than CBC.
Building Summary
Thesis Objective
Mechanical Depth
Structural Breadth
Electrical Breadth
Evaluation and Conclusion
fineartamerica.com

## Slide 15
Michael Gramarossa Northeastern Illinois University’s El Centro Mechanical Option
Building Summary
Thesis Objective
Mechanical Depth
  RTU Resize
  Energy Savings
  Emission Savings
Structural Breadth
Electrical Breadth
Evaluation and Conclusion
RTU Resize
System | CBC | IBC/IMC | % Saved
 | Req'd OA (CFM) | Req'd OA (CFM) | 
RTU-1 Total | 9260 | 5761 | 37.79%
RTU-2 Total | 10890 | 8292 | 23.86%
System Total | 20150 | 14053 | 30.26%
Ventilation Requirements
System | CBC |  | IBC/IMC | 
 | Cooling (Tons) | Supply Air (CFM) | Cooling (Tons) | Supply Air (CFM)
RTU-1 | 93 | 20,700 | 84 | 20,700
RTU-2 | 97 | 22,100 | 89 | 22,100
Total | 190 | 42,800 | 173 | 42,800
 |  | % Saved | -9.10% | 0%
Load Requirements

## Slide 16
Michael Gramarossa Northeastern Illinois University’s El Centro Mechanical Option
System | CBC | IBC/IMC | % Saved
 | Req'd OA (CFM) | Req'd OA (CFM) | 
RTU-1 Total | 9260 | 5761 | 37.79%
RTU-2 Total | 10890 | 8292 | 23.86%
System Total | 20150 | 14053 | 30.26%
Ventilation Requirements
System | CBC |  | IBC/IMC | 
 | Cooling (Tons) | Supply Air (CFM) | Cooling (Tons) | Supply Air (CFM)
RTU-1 | 93 | 20,700 | 84 | 20,700
RTU-2 | 97 | 22,100 | 89 | 22,100
Total | 190 | 42,800 | 173 | 42,800
 |  | % Saved | -9.10% | 0%
Load Requirements
Carrier model number chosen
RTU Resize
Building Summary
Thesis Objective
Mechanical Depth
  RTU Resize
  Energy Savings
  Emission Savings
Structural Breadth
Electrical Breadth
Evaluation and Conclusion
carrier.com

## Slide 17
Michael Gramarossa Northeastern Illinois University’s El Centro Mechanical Option
System | CBC | IBC/IMC | % Saved
 | Req'd OA (CFM) | Req'd OA (CFM) | 
RTU-1 Total | 9260 | 5761 | 37.79%
RTU-2 Total | 10890 | 8292 | 23.86%
System Total | 20150 | 14053 | 30.26%
Ventilation Requirements
System | CBC |  | IBC/IMC | 
 | Cooling (Tons) | Supply Air (CFM) | Cooling (Tons) | Supply Air (CFM)
RTU-1 | 93 | 20,700 | 84 | 20,700
RTU-2 | 97 | 22,100 | 89 | 22,100
Total | 190 | 42,800 | 173 | 42,800
 |  | % Saved | -9.10% | 0%
Load Requirements
Carrier model number chosen
Low Gas Heat Capacity: 527 MBH
High Gas Heat Capacity: 790 MBH
RTU Resize
Building Summary
Thesis Objective
Mechanical Depth
  RTU Resize
  Energy Savings
  Emission Savings
Structural Breadth
Electrical Breadth
Evaluation and Conclusion

## Slide 18
Michael Gramarossa Northeastern Illinois University’s El Centro Mechanical Option
or…
Fan Selection
RTU Resize
Building Summary
Thesis Objective
Mechanical Depth
  RTU Resize
  Energy Savings
  Emission Savings
Structural Breadth
Electrical Breadth
Evaluation and Conclusion
trane.com
trane.com

## Slide 19
Michael Gramarossa Northeastern Illinois University’s El Centro Mechanical Option
Fan Selection
or…
RTU Resize
Building Summary
Thesis Objective
Mechanical Depth
  RTU Resize
  Energy Savings
  Emission Savings
Structural Breadth
Electrical Breadth
Evaluation and Conclusion
trane.com
trane.com

## Slide 20
Michael Gramarossa Northeastern Illinois University’s El Centro Mechanical Option
RTU Schematic
RTU Resize
Building Summary
Thesis Objective
Mechanical Depth
  RTU Resize
  Energy Savings
  Emission Savings
Structural Breadth
Electrical Breadth
Evaluation and Conclusion

## Slide 21
Michael Gramarossa Northeastern Illinois University’s El Centro Mechanical Option
RTU Schematic
RTU Resize
Code | RTU Size | Cost (incl. O&P) | Location Factor | Adjusted Cost | Qty. of RTUs | Total Cost
CBC | 105 tons | $252,000 | 113.6% | $286,272 | 2 | $572,544
IBC/IMC | 90 tons | $225,500 | 113.6% | $256,168 | 2 | $512,336
Potential Savings
10.5%
$60,000
Building Summary
Thesis Objective
Mechanical Depth
  RTU Resize
  Energy Savings
  Emission Savings
Structural Breadth
Electrical Breadth
Evaluation and Conclusion

## Slide 22
Michael Gramarossa Northeastern Illinois University’s El Centro Mechanical Option
Annual Utility Usage
CBC |  |  | IBC/IMC |  | 
Elec Used (kWh) | NG Used (therms) | Total Utility Cost | Elec Used (kWh) | NG Used (therms) | Total Utility Cost
727,000 | 9,600 | $65,500 | 723,000 | 7,400 | $63,700
 |  | Savings | 0.5% | 29.5% | 2.9%
Electricity Cost Savings: 0.5%
Natural Gas Cost Savings: 29.5%
Total Utility Cost Savings: 2.9%
Electric & NG Cost Savings: $1800
Building Summary
Thesis Objective
Mechanical Depth
  RTU Resize
  Energy Savings
  Emission Savings
Structural Breadth
Electrical Breadth
Evaluation and Conclusion

## Slide 23
Michael Gramarossa Northeastern Illinois University’s El Centro Mechanical Option
Annual Utility Usage
Why are there more energy savings in the heating system than the cooling system?
CBC |  |  | IBC/IMC |  | 
Elec Used (kWh) | NG Used (therms) | Total Utility Cost | Elec Used (kWh) | NG Used (therms) | Total Utility Cost
727,000 | 9,600 | $65,500 | 723,000 | 7,400 | $63,700
 |  | Savings | 0.5% | 29.5% | 2.9%
CBC
IBC/IMC
Building Summary
Thesis Objective
Mechanical Depth
  RTU Resize
  Energy Savings
  Emission Savings
Structural Breadth
Electrical Breadth
Evaluation and Conclusion

## Slide 24
Michael Gramarossa Northeastern Illinois University’s El Centro Mechanical Option
Annual Utility Usage
Why are there more energy savings in the heating system than the cooling system?
Cooling Degree Days | 842
Heating Degree Days | 6311
CBC |  |  | IBC/IMC |  | 
Elec Used (kWh) | NG Used (therms) | Total Utility Cost | Elec Used (kWh) | NG Used (therms) | Total Utility Cost
727,000 | 9,600 | $65,500 | 723,000 | 7,400 | $63,700
 |  | Savings | 0.5% | 29.5% | 2.9%
CBC
IBC/IMC
Building Summary
Thesis Objective
Mechanical Depth
  RTU Resize
  Energy Savings
  Emission Savings
Structural Breadth
Electrical Breadth
Evaluation and Conclusion

## Slide 25
Michael Gramarossa Northeastern Illinois University’s El Centro Mechanical Option
Annual Utility Usage
Chart: Monthly Electricity Usage
| Jan. | Feb. | Mar. | Apr. | May. | Jun. | Jul. | Aug. | Sept. | Oct. | Nov. | Dec.
CBC | 47653 | 42833 | 47971 | 51416 | 67751 | 77829 | 82507 | 85721 | 70043 | 59409 | 46192 | 47579
IBC/IMC | 48012 | 43149 | 47998 | 52299 | 67914 | 76169 | 80446 | 83348 | 69186 | 60625 | 46175 | 47710
Chart: Monthly Natural Gas Usage
| Jan. | Feb. | Mar. | Apr. | May. | Jun. | Jul. | Aug. | Sept. | Oct. | Nov. | Dec.
CBC | 3230 | 2013 | 1341 | 321 | 22 | 0 | 0 | 0 | 3 | 192 | 854 | 1627
IBC/IMC | 2464 | 1464 | 1012 | 308 | 21 | 0 | 0 | 0 | 3 | 186 | 727 | 1231
CBC |  |  | IBC/IMC |  | 
Elec Used (kWh) | NG Used (therms) | Total Utility Cost | Elec Used (kWh) | NG Used (therms) | Total Utility Cost
727,000 | 9,600 | $65,500 | 723,000 | 7,400 | $63,700
 |  | Savings | 0.5% | 29.5% | 2.9%
CBC
IBC/IMC
Building Summary
Thesis Objective
Mechanical Depth
  RTU Resize
  Energy Savings
  Emission Savings
Structural Breadth
Electrical Breadth
Evaluation and Conclusion

## Slide 26
Michael Gramarossa Northeastern Illinois University’s El Centro Mechanical Option
Annual Utility Usage
Chart: Monthly Utility Costs (Elec. & NG)
| Jan. | Feb. | Mar. | Apr. | May. | Jun. | Jul. | Aug. | Sept. | Oct. | Nov. | Dec.
CBC | 5831.1074 | 4751.4059 | 4685.802 | 4543.9426 | 5815.5245 | 6179.6226 | 6724.3205 | 7071.9825 | 5802.5694 | 4912.08 | 4341.3332 | 4871.8285
IBC/IMC | 5332.0776 | 4406.9877 | 4456.292 | 4607.8164 | 5828.424 | 6047.8186 | 6556.349 | 6876.21 | 5731.6098 | 5004.38 | 4244.5945 | 4593.693
CBC |  |  | IBC/IMC |  | 
Elec Used (kWh) | NG Used (therms) | Total Utility Cost | Elec Used (kWh) | NG Used (therms) | Total Utility Cost
727,000 | 9,600 | $65,500 | 723,000 | 7,400 | $63,700
 |  | Savings | 0.5% | 29.5% | 2.9%
CBC
IBC/IMC
Building Summary
Thesis Objective
Mechanical Depth
  RTU Resize
  Energy Savings
  Emission Savings
Structural Breadth
Electrical Breadth
Evaluation and Conclusion

## Slide 27
Michael Gramarossa Northeastern Illinois University’s El Centro Mechanical Option
Emission Savings
Emission Savings ~37,000 lbs. CO2e per year
Building Summary
Thesis Objective
Mechanical Depth
  RTU Resize
  Energy Savings
  Emission Savings
Structural Breadth
Electrical Breadth
Evaluation and Conclusion

## Slide 28
Michael Gramarossa Northeastern Illinois University’s El Centro Mechanical Option
Structural Breadth
Building Summary
Thesis Objective
Mechanical Depth
Structural Breadth
  RTU-2
  RTU-1
  Conclusion
Electrical Breadth
Evaluation & Conclusion
Will smaller RTU’s designed according to the IBC lead to a reduction in structural steel?

## Slide 29
Michael Gramarossa Northeastern Illinois University’s El Centro Mechanical Option
Structural Breadth
Load Type | Material | Weight (psf)
Dead Load | PVC Roof | 10
 | 1/2" Cover Board | 2
 | R-30 Insulation Board | 2
 | Galvanized Metal Deck | 2
 | Misc. (lights, duct, PV array, etc.) | 10
Live Load or Snow Load | Live Load | 20
 | Snow Load | 25
Total | Dead Load | 26
 | Snow Load | 25
Building Summary
Thesis Objective
Mechanical Depth
Structural Breadth
  RTU-2
  RTU-1
  Conclusion
Electrical Breadth
Evaluation & Conclusion

## Slide 30
Michael Gramarossa Northeastern Illinois University’s El Centro Mechanical Option
N
C8x11.5
C8x11.5
Building Summary
Thesis Objective
Mechanical Depth
Structural Breadth
  RTU-2
  RTU-1
  Conclusion
Electrical Breadth
Evaluation & Conclusion
RTU-2 Analysis

## Slide 31
Michael Gramarossa Northeastern Illinois University’s El Centro Mechanical Option
N
C8x11.5
C8x11.5
Building Summary
Thesis Objective
Mechanical Depth
Structural Breadth
  RTU-2
  RTU-1
  Conclusion
Electrical Breadth
Evaluation & Conclusion
RTU-2 Analysis

## Slide 32
Michael Gramarossa Northeastern Illinois University’s El Centro Mechanical Option
N
C8x11.5
C8x11.5
Building Summary
Thesis Objective
Mechanical Depth
Structural Breadth
  RTU-2
  RTU-1
  Conclusion
Electrical Breadth
Evaluation & Conclusion
RTU-2 Analysis

## Slide 33
Michael Gramarossa Northeastern Illinois University’s El Centro Mechanical Option
N
C8x11.5
C8x11.5
(Max M = 358 kip-ft)
Building Summary
Thesis Objective
Mechanical Depth
Structural Breadth
  RTU-2
  RTU-1
  Conclusion
Electrical Breadth
Evaluation & Conclusion
RTU-2 Analysis

## Slide 34
Michael Gramarossa Northeastern Illinois University’s El Centro Mechanical Option
Building Summary
Thesis Objective
Mechanical Depth
Structural Breadth
  RTU-2
  RTU-1
  Conclusion
Electrical Breadth
Evaluation & Conclusion
RTU-1 Analysis
These beams are not reduced in size because the structural engineer did not use a smaller beam than W12x26.

## Slide 35
Michael Gramarossa Northeastern Illinois University’s El Centro Mechanical Option
Building Summary
Thesis Objective
Mechanical Depth
Structural Breadth
  RTU-2
  RTU-1
  Conclusion
Electrical Breadth
Evaluation & Conclusion
Structural Breadth Conclusion
Beam Size | Existing Design | New Design | Cost ($/LF)
 | Length (ft) | Length (ft) | 
C8x11.5 | 151 | 124 | $83.68
W21x44 | 0 | 51 | $84.21
W21x48 | 51 | 0 | $94.34
Total Cost | $17,447 | $14,671
New design leads to $2,800 in savings

## Slide 36
Michael Gramarossa Northeastern Illinois University’s El Centro Mechanical Option
Building Summary
Thesis Objective
Mechanical Depth
Structural Breadth
  RTU-2
  RTU-1
  Conclusion
Electrical Breadth
Evaluation & Conclusion
Structural Breadth Conclusion
Total Cost | $17,447 | $14,671
New design leads to $2,800 in savings
Structural steel savings are a result of a different design approach.
There would be negligible structural steel savings associated with designing to the IBC rather than the CBC with regards to the mechanical system.
Beam Size | Existing Design | New Design | Cost ($/LF)
 | Length (ft) | Length (ft) | 
C8x11.5 | 151 | 124 | $83.68
W21x44 | 0 | 51 | $84.21
W21x48 | 51 | 0 | $94.34

## Slide 37
Michael Gramarossa Northeastern Illinois University’s El Centro Mechanical Option
Building Summary
Thesis Objective
Mechanical Depth
Structural Breadth
Electrical Breadth
Evaluation & Conclusion
Electrical Breadth
Will smaller RTU’s designed according to the IBC lead to a reduction in electrical wiring?

## Slide 38
Michael Gramarossa Northeastern Illinois University’s El Centro Mechanical Option
Building Summary
Thesis Objective
Mechanical Depth
Structural Breadth
Electrical Breadth
Evaluation & Conclusion
Electrical Breadth
New Design
Existing Design

## Slide 39
Michael Gramarossa Northeastern Illinois University’s El Centro Mechanical Option
Building Summary
Thesis Objective
Mechanical Depth
Structural Breadth
Electrical Breadth
Evaluation & Conclusion
Electrical Breadth
New Design
The same as structural, using the IBC in lieu of the CBC will lead to minimal to no electrical cost savings
The savings associated were a result of a different design strategy

## Slide 40
Michael Gramarossa Northeastern Illinois University’s El Centro Mechanical Option
Building Summary
Thesis Objective
Mechanical Depth
Structural Breadth
Electrical Breadth
Evaluation & Conclusion
  City of Chicago Study
  Overall Evaluation
  Acknowledgements
City of Chicago Study
envato.com

## Slide 41
Michael Gramarossa Northeastern Illinois University’s El Centro Mechanical Option
Building Summary
Thesis Objective
Mechanical Depth
Structural Breadth
Electrical Breadth
Evaluation & Conclusion
  City of Chicago Study
  Overall Evaluation
  Acknowledgements
City of Chicago Study
Reduce Chicago’s greenhouse gas emissions by 80% below 1990 levels by 2050
    Energy Efficient Buildings (30%)
    Clean & Renewable Energy Sources (34%)
    Improved Transportation Options (23%)
    Reduction Waste & Industrial Pollution (13%)
    Adaptation
envato.com

## Slide 42
Michael Gramarossa Northeastern Illinois University’s El Centro Mechanical Option
Building Summary
Thesis Objective
Mechanical Depth
Structural Breadth
Electrical Breadth
Evaluation & Conclusion
  City of Chicago Study
  Overall Evaluation
  Acknowledgements
City of Chicago Study
Chicago Building Energy
$3 billion per year
Potential Savings 2.9%
$87 million per year
envato.com

## Slide 43
Michael Gramarossa Northeastern Illinois University’s El Centro Mechanical Option
Building Summary
Thesis Objective
Mechanical Depth
Structural Breadth
Electrical Breadth
Evaluation & Conclusion
  City of Chicago Study
  Overall Evaluation
  Acknowledgements
City of Chicago Study
Chicago Building Energy
$3 billion per year
Potential Savings 2.9%
$87 million per year
Chicago Building Emissions
63 billion lbs. CO2e per year
Potential Savings 2.42%
1.5 billion lbs. CO2e per year
Equivalent to taking 184,000 cars off of the road

## Slide 44
Michael Gramarossa Northeastern Illinois University’s El Centro Mechanical Option
Building Summary
Thesis Objective
Mechanical Depth
Structural Breadth
Electrical Breadth
Evaluation & Conclusion
  City of Chicago Study
  Overall Evaluation
  Acknowledgements
Overall Evaluation
  Possible Mechanical First Cost Savings
  No Structural or Electrical Cost Savings
  Energy Cost Savings 2.9%
  Emission Savings 2.42%

## Slide 45
Michael Gramarossa Northeastern Illinois University’s El Centro Mechanical Option
Building Summary
Thesis Objective
Mechanical Depth
Structural Breadth
Electrical Breadth
Evaluation & Conclusion
  City of Chicago Study
  Overall Evaluation
  Acknowledgements
Overall Evaluation
  Possible Mechanical First Cost Savings
  No Structural or Electrical Cost Savings
  Energy Cost Savings 2.9%
  Emission Savings 2.42%
  Minimal Impact on a small scale
  Big impact on a large scale

## Slide 46
Michael Gramarossa Northeastern Illinois University’s El Centro Mechanical Option
Building Summary
Thesis Objective
Mechanical Depth
Structural Breadth
Electrical Breadth
Evaluation & Conclusion
  City of Chicago Study
  Overall Evaluation
  Acknowledgements
Acknowledgements
  Primera Engineers
  Professor Freihaut
  Penn State AE Faculty and Staff
  Friends and Family
  And of course,

## Slide 47
Michael Gramarossa Northeastern Illinois University’s El Centro Mechanical Option
Building Summary
Thesis Objective
Mechanical Depth
Structural Breadth
Electrical Breadth
Evaluation & Conclusion
  City of Chicago Study
  Overall Evaluation
  Acknowledgements
Acknowledgements
  Primera Engineers
  Professor Freihaut
  Penn State AE Faculty and Staff
  Friends and Family
  And of course, President Obama

## Slide 48
Michael Gramarossa Northeastern Illinois University’s El Centro Mechanical Option
Questions?
Summary of Savings | Energy Savings |  | Annual Cost Savings |  | Emission Savings | 
 | % | kBtu/year | % | $/year | % | lbs. CO2e/yr
NEIU El Centro | 6.70% | 232,000 | 2.90% | $1,850 | 2.42% | 33,600
City of Chicago | 6.70% | 10.4 billion | 2.90% | $87 million | 2.42% | 1.5 billion
CBC
IBC/IMC

## Slide 49
Michael Gramarossa Northeastern Illinois University’s El Centro Mechanical Option
Electrical Appendix
System | Equipment | V/PH/Hz | FLA | MOCP | kVA | Wire (Copper) (THWN) | Ground (Copper) | Conduit (EMT)
Existing | RTU-1 | 460/3/60 | 149 | 150 A | 124 | (4) #2/0 | #6 | 2"
 | RTU-2 | 460/3/60 | 149 | 150 A | 124 | (4) #2/0 | #6 | 2"
 | CU-1 | 460/3/60 | 227 | 250 A | 189 | (4) 350 kcmil | #4 | 3 1/2"
 | CU-2 | 460/3/60 | 227 | 250 A | 189 | (4) 350 kcmil | #4 | 3 1/2"
New | RTU-1 | 460/3/60 | 257 | 300 A | 214 | (4) 300 kcmil | #4 | 2 1/2"
 | RTU-2 | 460/3/60 | 257 | 300 A | 214 | (4) 300 kcmil | #4 | 2 1/2"
Table 26 – Existing and New Branch Wire Sizing for RTUs
System | Panel Label | Equipment Served | Voltage | FLA | kVA | MOCP | Feeder Size (Copper, THWN, EMT)
Existing | DPM3-1 | RTU-1 & RTU-2 | 480/277 | 298 | 248 | 600 A | (2) sets: 4-350 kcmil, #1/0 Grd, 3 1/2" C
New | DPM3-1 | RTU-1 & RTU-2 | 480/277 | 514 | 428 | 800 A | (3) sets: 4-300 kcmil, #2 Grd, 2 1/2" C
Table 27 – Existing and New Feeder Sizing for RTUs
1.9256 in2 ∴ use 2 ½” Conduit
1.959 in2 ∴ use 2 ½” Conduit

## Slide 50
Michael Gramarossa Northeastern Illinois University’s El Centro Mechanical Option
City of Chicago Appendix
Total Amount Chicago Spends on Building Energy ($) | Potential Savings (%) | Potential Savings ($)
$3 billion | 2.90% | $87 million
Total Amount of Energy Used by Chicago Buildings (kBtu/year) | Potential Savings (%) | Potential Savings ($/year)
155 billion kBtu | 6.70% | 10.4 billion kBtu
Unit | Total Pollutants Produced by Chicago Buildings (CO2e/year) | Potential Savings (%) | Potential Savings (CO2e/year)
lbs. CO2e/year | 63 billion lbs. | 2.42% | 1.5 billion lbs.
tons CO2e/year | 31.6 million tons | 2.42% | 765,000 tons
Equivalent of Cars on the Road per year | 7.6 million cars | 2.42% | 184,000 cars
Rank | City | Country | No. of Skyscrapers
1 | Hong Kong | China | 302
2 | New York City | United States | 235
3 | Dubai | United Arab Emirates | 148
4 | Shanghai | China | 126
5 | Chicago | United States | 115
6 | Tokyo | Japan | 112
7 | Chongqing | China | 94
8 | Guangzhou | China | 93
9 | Shenzhen | China | 83
10 | Singapore | Singapore | 79
Building Type | kBTU/ft2/yr
Large Office | 43
Medium Office | 48
Small Office | 51
Warehouse | 24
Stand-alone Retail | 81
Strip Mall | 85
Primary School | 65
Secondary School | 76
Supermarket | 195
Quick Service Restaurant | 657
Hospital | 148
Outpatient Facility | 271
Small Hotel | 80
Large Hotel | 138
Mid-Rise Apartment | 47
NEIU El Centro* | 62