Technical Report 1

Executive Summary

This report provides a detailed description and analysis of the existing structural systems at the Heart Hospital. Swedish American Hospital recently completed phase 2 of a 3 phase construction project on their grounds. Part of phase 2 was the construction of the new Heart and Vascular Center, also known as the Heart Hospital.

First, an in depth explanation of each of the main structural systems present in the building is provided. Typical sizes of framing and layouts are listed to help readers visualize a general image of the structure. A summary of the building codes used in the original design is listed, followed by a list of more recent building codes that will be used to analyze the existing structure.

Typical framing plans and elevations are provided to explain the buildings structural components in three dimensions. Brief summaries are included to help convey any elements that could not be shown on the diagrams. Building Dead Loads, Live Loads and Lateral Loads are tabulated and compiled in a set of tables, with corresponding code references as necessary. Spot checks of building elements, such as a beam, girder, and column, are conducted using the calculated gravity and lateral values. LRFD load factors are used in all calculations since the vast majority of the building’s structural elements are steel. A simplified check of a lateral framing element is computed to check the validity of the design load assumptions and lateral load calculations. Further assumptions for the gravity element checks and frame analysis can be found in the detailed hand calculations located in the appendix of this report. Additional calculations are available upon request.

Table of Contents

Executive Summary	1

Structural System Overview	3

Codes	5

Material Strengths	5

Typical Framing Plans	6

Design Theory	10

Building Loads and Loading Diagrams	11
      Live Loads
      Snow Loads
      Dead Loads
      Seismic Loads
      Wind Design Loads

Framing Check	14
      Beam Check
      Girder Check
      Column Check
      Lateral Frame Check

Appendix	16

Structural System Overview

Floor System:

The typical building floor framing system is made up of beams and girders acting compositely with a concrete floor slab. Floor sections show 3”-20 gauge LOK Floor galvanized metal deck with 3¼” of lightweight concrete (110 pcf) resting on the steel framing below. Composite action is achieved through 5” long ¾” diameter shear studs welded to the steel framing. Concrete is reinforced with 6x6-W5xW5 welded wire fabric. The span of the metal deck varies depending on the bay location. However, the direction is limited to east-west or northeast-southwest.  This assembly has a 2 hour fire rating without the use of spray on fireproofing.

There is no “typical” bay in the structural framing system. However, columns located on the wings are spaced approximately 22’-7 ½” on center. Columns in the interior core area are spaced approximately 32’-0” on center with additional columns located around the core perimeter framing into the wings. The most common and longest span is 32’-0”. Typical beam sizes range from W12x14’s to W27x146 with the larger beams acting as part of the moment framing system.

Roof System:

The roof framing system is very similar to the building floor framing system. Composite design is still used with 3 ¼” of lightweight concrete and 3”-20gauge LOK Floor metal deck on top of steel framing. Deeper steel beams and girders are used to help carry the heavier loads of the mechanical equipment on the roof.

The lobby roof is different from the typical roof framing. It does not use composite action and instead has a 1 ½” deep 20 gauge metal deck spanning north-south. Lower portions of the roof use a 3” deep 20 gauge metal deck to accommodate heavier snow loads and drifts.

Lateral System:

The lateral load resisting system consists of steel moment frames. The majority of the moment frames extend around the perimeter of the building with a few added moment frames on the interior to help stiffen the structure. Larger girders are framed into columns with bolted flange plate moment connections. The prefabricated steel pieces were bolted in place rather than welded to eliminate the need of preheating for welds. Shear walls were not part of the original design analysis; therefore, masonry cores such as the elevator and stairwell cores were not designed for lateral support.

Foundation

The basement footprint is approximately one half of the square footage of the first floor plan. Hence, there are two slabs on grade: one for the basement and one for part of the first floor. Each slab on grade is 5” thick normal weight concrete (145pcf) with 4x4-W5xW5 welded wire fabric reinforcement.

Interior steel columns rest on spread footings with an allowable soil bearing capacity of 4ksf. Exterior columns and basement walls rest on continuous strip footings. Reinforced concrete pilasters are located where exterior columns rest on the basement wall. Footings below columns in the interior core area extend approximately 18’ deep whereas the perimeter strip footings and footings located beneath the wings extend approximately 8’ deep. All footings are required to extend a minimum of 4’ deep for frost protection.

Columns:

Columns are laid out on two different intersecting grids: one running east-west and the other running northwest-southeast. All columns are ASTM A992 Grade 50 wide flange steel shapes. Columns are spliced between the 3rd and 4th floor. Columns acting as part of a moment frame are spliced 5’-6” above the 3rd floor elevation. Columns acting only as gravity columns are spliced 4’-6” above the 3rd floor elevation. All interior columns that extend to the basement level are also spliced 5’-6” above the 1st floor elevation. Future columns for the 6th and 7th floors are designed to be spliced with existing columns at the 5th floor elevation (current mechanical floor and roof).

Codes

Original Design Codes:

- International Building Code (IBC) 2003

  - with City of Rockford, IL amendment

- American Society of Civil Engineers (ASCE)

  - ASCE 7-02 - Minimum Design Loads for Buildings and Other Structures

- American Concrete Institute (ACI)

  - ACI 318-02 - Building Code Requirements for Structural Concrete

  - ACI 530-02 – Building Code Requirements for Masonry Structures

- American Institute of Steel Construction (ASIC)

  - LRFD 1999 - Load and Resistance Factor Design Specification for Structural Steel Buildings

  - AISC 341-02 – Seismic Provisions for Structural Steel Buildings

Thesis Design Codes:

    - International Building Code (IBC) 2006

    - American Society of Civil Engineers (ASCE)

  - ASCE 7-05 - Minimum Design Loads for Buildings and Other Structures

    - American Concrete Institute (ACI)

  - ACI 318-05 – Building Code Requirements for Structure Concrete

Material Strengths

Concrete

Normal Weight Concrete (columns, walls, foundations, slabs on grade)……...…4000psi

Light Weight Concrete (floor slabs on metal deck)………………………………4000psi

Reinforcement ………………………………………………………………………60ksi

Structural Steel

Wide Flanges and Channels ………………………………………………………...50ksi

Angles, Bars and Plates……………………………………………………………...36ksi

Hollow Structural Sections (HSS)………………………………………………….. 46ksi

Bolts (A325X or A490X)………………………………………………………….3/4”dia

Shear Studs (5”long)……………………………………………………………… 3/4”dia

Masonry

Design Strength (F’m)…………………………………………………………….2000psi

Block……………………………………………………………………………...4000psi

Typical Framing Plans

Foundation Plans

The building is supported on both spread and strip footings. Spread footings usually support a single interior column. Spread footings located at the corners of the building can support two or three columns. Strip footings extend around the perimeter of the building and below the basement walls (the basement is approximately half the area of the building footprint).

Two slabs on grade are poured for the Heart and Vascular Center. The first slab is at the basement elevation and located at the center core of the building. The area of this slab is approximately 12,500 sq. ft., which is about half of the overall building footprint (25,000 sq.ft.).

The basement walls are assumed to be single span that is laterally supported by the slab on grade at the base and the first floor framing at the top. They are designed to resist load from the lateral earth pressure.

Figure 1: Ground Floor Plan highlighting foundation systems

Strip footings running around the perimeter of the building are highlighted in RED. The First Floor slab on grade (not including the Lobby) is outlined and labeled in BLUE. The area of the basement slab on grade is labeled in ORANGE.

Typical Floor Plans

Open floor plans are achieved through the use of stiff moment frames. This allows for more flexible interior spaces and maximizes the use of natural light. Composite action used to maximize the strength of the structural steel and concrete floor slab. Floor systems utilize 3” galvanized LOK Floor decks with 3¼” of lightweight concrete resting on a grid of beams and girders. The concrete and metal deck system is designed to be unshored for a two span condition. Single spans should be shored unless otherwise specified. The maximum distance for a single span is approximately 11’-6”.

Floor framing is oriented north-south and east-west for the wings of the Heart and Vascular Center and the entrance lobby. The framing at the central core is oriented diagonally northwest-southeast and northeast-southwest. Metal deck installed on the hospital wings spans east-west, and spans northeast-southwest at the central core. All concrete and metal deck floor systems are assumed to be rigid systems.

Figure 2: Typical Floor system showing layout of beams and girders

Lateral Framing System

Swedish American Hospital’s new Heart and Vascular Center is laterally supported with steel moment frames. The Frames are designed to resist wind and seismic loads. Pieces of these frames are prefabricated then bolted together onsite. Flange plate bolted connections are used in place of welded connections (see Appendix A for details). Bolted connections eliminate the need for preheating steel for welded connections. Since steel erection began in mid February, eliminating the need for preheating helped speed up the erection process and keep the project on schedule.

The majority of the moment frames lie around the perimeter of the building, with some interior moment frames added to help stiffen the structure and reduce drift. Less interior moment frames help reduce the required depth of steel in interior spaces to minimize conflicts with HVAC systems. Moment frames allow for a more open architectural floor plan. Swedish American uses their open floor plan to help increase the amount of natural light that reaches their interior spaces. Braced frames and shear walls could create potential problems with door and window openings. All frames are assumed to be pin-supported on spread footings and concrete piers at the basement level.

Figure 3: Framing Plan with Highlighted Moment Frames

*Typical moment frames are outlined in RED.

- GREEN arrows represent concentrated live load from beam framing.

- BLUE arrows represent concentrated dead load from beam framing.

- RED arrows represent lateral load from wind or seismic forces acting at the floor level.

Floor Loading:

The steel deck near column line K runs parallel to the frame. Floor loads are transferred from the slab and deck to beams (typically spanning 18’ to 22’, also spanning 32’ in some locations). These beams run perpendicular to the girders along column line K and frame in near the third points.

When analyzing beams or girders running perpendicular to the steel deck, the load is considered a distributed load along the members’ length. When the framing is parallel to the steel deck (as it is for the majority of the girders), the load is considered a concentrated point load where the beam frames into the girder.

Lateral Loading:

For seismic loading, the total base shear is calculated using ASCE 7-05 Sections 11 and 12 (see Seismic Load Table on page 12 and seismic load calculations in Appendix B). The Heart and Vascular Center has a base shear of approximately 875k. This base shear is divided over the entire story height based on the height and weight of each story over the entire height and weight of the structure. This effective story shear is assumed to be taken at the floor level of each story. The shear at the lowest level is small but increases with height for my building.

For wind pressures, the windward pressure acting along the height of the structure is in the form of a parabolic curve. A conservative assumption is to break the curve into a rectangular grid and find the effective pressure acting on an individual story. Windward pressures are calculated using equation 6.19 in ASCE 7-05 Section 6 (see the Wind Design Load Tables on page 13 and Appendix C for wind pressures, diagrams, and Gust Factors). Leeward pressure is assumed to be a constant along the back of the building and calculated using the total building height. Wind pressures are calculated in two main directions (usually acting perpendicular to the building face). Base shears resulting from wind for the Heart Hospital were 555k (N-S direction) and 369k (E-W direction). Therefore, seismic controls the lateral design.

Design Theory

Moment Frame vs Braced Frame or Shear Walls

Moment frames were designed in place of braced frames or shear walls to create an open flexible floor plan. Swedish American Hospital wanted to option to “re-program” various floors and re-layout different floor plans. Braced frames and shear walls are a hindrance when trying to re-layout a floor plan and will minimize the number of available floor plan options.

Swedish American Hospital and Perkins and Will Architects also liked the uniform appearance along the façade faces created by the moment frames. Braced frames could interrupt the uniformity of a façade and could obstruct patient views out their windows. The hospital was willing to accept the extra expenses in exchange for a more aesthetically appealing façade and future flexibility in floor arrangements and layouts.

Possible shear walls exist at the northwest and southeast corners of the building where the stairwells and elevator core lie. However, shear walls were not incorporated into the structural design of the Heart and Vascular Center. Simpson Gumpertz and Heger Inc., the Structural Engineers, prefer to only classify and design one type of lateral system instead of a dual system. For this project, they chose to only analyze and design the steel moment frames. These vertical cores could provide a small contribution to the building’s overall stiffness, but were not taken into account during design.

4 Floors vs 7 Floors

The Swedish American Hospital’s new Heart and Vascular Center is part of phase 2 in a 3 phase construction project on the hospital grounds. The original 7 floors where designed based on a “Certificate of Need”. A Certificate of Need establishes the number of patient rooms required for a hospital based on the local increasing population. Therefore, the new Heart and Vascular center is required to handle that patient increase and must be designed for that load. However, other local hospitals and medical facilities share some of that patient load and is the reason the existing Heart and Vascular Center is only 4 stories.

Phase 3 of the Swedish American construction project is the addition of the 3 floors on top of the new Heart and Vascular Center. However, this causes a problem. To begin construction above an existing medical facility, the facility must first be shut down and all patients evacuated and transferred to another facility. Shutting down the Heart Hospital could cause potential problems with relocating critical patients and getting adequate care to other patients. Closing the hospital, even temporarily, would redirect numerous patients to other local hospitals possibly flooding their medical facilities. Not to mention, many Heart and Vascular Center employees may be without a job (or have a decrease in hours) until construction is nearing completion.

Building Loads and Loading Diagrams

Floor Live Loads

| Loaded Area | Building Design Load | ASCE 7-05 Section 4 |
| --- | --- | --- |
| Basement Floor | 100 psf | Table 4-1 |
| First Floor | 100 psf | Table 4-1 |
| Typical Floors (2nd, 3rd, 4th, 6th, 7th) | 80 psf | Table 4-1 |
| Mechanical/Roof (5th Floor) | 150 psf | Set by SAH*, Engineers |
| Stairwells | 100 psf | Table 4-1 |
| Roof (8th Future Roof) | 25 psf | ASCE 7-05 Section 7 (Snow) |

* SAH – Swedish American Hospital

Roof Snow Loads (Live Load)

| Item | Design Load | Code References |
| --- | --- | --- |
| Roof Live Load | 25 psf | ASCE 7-05 Section 7 |
| Ground Snow Load | 30 psf | ASCE 7-05 Figure 7-1 |
| Additional Drift Load | 50.4 psf | ASCE 7-05 Section 7-7 |
| Exposure Factor (Ce) | 1.0 | ASCE 7-05 Table 7-2 |
| Importance Factor (I) | 1.2 | ASCE 7-05 Table 7-4 |
| Thermal Factor (Cf) | 1.0 | ASCE 7-05 Table 7-3 |

Dead Loads

Typical Floors 1 though 4 and Future Floors 6 and 7

| Item | Design Load |
| --- | --- |
| Partitions | 10 psf |
| Steel Deck with LWC Slab | 48 psf |
| Ponding due to Deflection | 5 psf |
| Steel Self Weight | 15 psf |
| MEP, Misc. | 12 psf |
| Total | 90 psf |

5th Floor (Roof/Mechanical)

| Item | Design Load |
| --- | --- |
| Partitions | 0 psf |
| Permanent Equipment | 50 psf |
| Steel Deck with LWC Slab | 48 psf |
| Ponding due to Deflection | 5 psf |
| Steel Self Weight | 15 psf |
| MEP, Misc. | 12 psf |
| Total | 130 psf |

8th Floor (Future Roof) *

| Item | Design Load |
| --- | --- |
| Permanent Equipment | 0 psf |
| Steel Deck with LWC Slab | 48 psf |
| Ponding due to Deflection | 5 psf |
| Steel Self Weight | 15 psf |
| MEP, Misc. | 12 psf |
| Total | 80 psf |

Other Areas (lobby roof, Stair tower roof) *

| Item | Design Load |
| --- | --- |
| Metal Deck, Insulation, Roofing | 25 psf |
| Steel Self Weight | 15 psf |
| MEP, Misc. | 5 psf |
| Total | 45 psf |

Wall Dead Loads

| Item | Design Load |
| --- | --- |
| Exterior Wall Precast Panel | 85 psf |
| Exterior Wall Brick | 50 psf |
| Exterior Aluminum Curtain Wall | 15 psf |
| Shaft Walls around openings | 20 psf |
| Stair Walls around openings | 80 psf |

* Snow mass is not included in Dead Loads, but a 5 psf snow load is included for seismic massing (ASCE 7-05 Section 12.7.2).

Seismic Loads

| Item | Design Value | Code Reference |
| --- | --- | --- |
| Occupancy Category | IV | ASCE 7-05 Table 1-1 |
| Site Class | D | * From Geotechnical Report |
| Spectral Acceleration for Short Periods (Ss) | 0.17g | * From Geotechnical Report |
| Spectral Acceleration for One Sec. Periods (S1) | 0.06g | * From Geotechnical Report |
| Damped Design for Short Periods (Sds) | 0.1813g | ASCE 7-05 Section 11.4.4 |
| Damped Design for One Sec. Periods (Sd1) | 0.096g | ASCE 7-05 Section 11.4.4 |
| Seismic Design Category | C | ASCE 7-05 Section 11.6.1.1 |
| Seismic Force Resisting System | Ordinary Steel Moment Frames | ASCE 7-05 Table 12.2-1 |
| Response Modification Factor (R) | 3.5 | ASCE 7-05 Table 12.2-1 |
| System Overstrength Factor (Ω) | 3.0 | ASCE 7-05 Table 12.2-1 |
| Deflection Amplification Factor (Cd) | 3.0 | ASCE 7-05 Table 12.2-1 |
| Importance Factor | 1.5 | ASCE 7-05 Table 11.5-1 |
| Approximate Period (Ta) | 1.106 | ASCE 7-05 Section 12.8.2.1 |
| Seismic Response Coefficient (Cs) | 0.037 | ASCE 7-05 Section 12.8.1.1 |
| Building Mass | 23,650k | * From Massing Calculations |
| Design Base Shear | 875k |  |

Vertical Distribution of Seismic Loads

ASCE 7-05 Section 12.8.3

| Level | h (in ft) | W in kips | wxhxk | Cvx | Fx |
| --- | --- | --- | --- | --- | --- |
| 8th floor future Roof | 99.17 | 2568 | 1025315 | 0.24 | 208.79 |
| 7th floor future | 85.83 | 2977 | 984759 | 0.23 | 200.53 |
| 6th floor (future) | 72.50 | 3376 | 896231 | 0.21 | 182.50 |
| 5th floor mechanical | 52.50 | 4047 | 705500 | 0.16 | 143.67 |
| 4th floor | 39.17 | 3091 | 367848 | 0.09 | 74.91 |
| 3rd floor | 25.83 | 3342 | 231248 | 0.05 | 47.09 |
| 2nd floor | 12.50 | 3200 | 85985 | 0.02 | 17.51 |
| 1st floor | 0.00 | 1049 | 0 | 0.00 | 0.00 |
|  |  | 23650k | 4296886 |  | 875k |

Design Base Shear (V) = 875 k

k (by interpolation) = 1.303

Wind Design loads

| Level | Total Height | Kz | q | Wind Pressures (psf) |
| --- | --- | --- | --- | --- |
|  |  |  |  | N-S Windward | N-S Leeward | N-S Side Wall | E-W Windward | E-W Leeward | E-W Side Wall |
| Roof | 99.17 | 1.26 | 25.54 | 17.26 | -10.79 | -15.10 | 17.43 | -8.71 | -15.25 |
| 7 | 85.83 | 1.225 | 24.83 | 16.78 | -10.79 | -15.10 | 16.94 | -8.71 | -15.25 |
| 6 | 72.50 | 1.18 | 23.92 | 16.17 | -10.79 | -15.10 | 16.32 | -8.71 | -15.25 |
| 5 | 52.5 | 1.1 | 22.30 | 15.07 | -10.79 | -15.10 | 15.21 | -8.71 | -15.25 |
| 4 | 39.17 | 1.04 | 21.08 | 14.25 | -10.79 | -15.10 | 14.38 | -8.71 | -15.25 |
| 3 | 25.83 | 0.94 | 19.05 | 12.88 | -10.79 | -15.10 | 13.00 | -8.71 | -15.25 |
| 2 | 12.5 | 0.85 | 17.23 | 11.64 | -10.79 | -15.10 | 11.76 | -8.71 | -15.25 |

| Level | Eff. Height | Wind Design (NS - EW) |
| --- | --- | --- |
|  |  | Load (kips) | Shear (kips) | Moment (ft-k) |
|  |  | N-S | E-W | N-S | E-W | N-S | E-W |
|  |  | 230' | 165' | 230' | 165' | 230' | 165' |
| Roof | 6.67 | 43 | 29 | 0 | 0 | 4264 | 2851 |
| 7 | 13.33 | 85 | 57 | 43 | 29 | 7318 | 4889 |
| 6 | 16.67 | 104 | 70 | 128 | 86 | 7576 | 5053 |
| 5 | 16.67 | 101 | 67 | 233 | 155 | 5314 | 3534 |
| 4 | 13.33 | 78 | 52 | 334 | 223 | 3056 | 2026 |
| 3 | 13.33 | 75 | 49 | 412 | 274 | 1928 | 1273 |
| 2 | 12.92 | 68 | 45 | 487 | 324 | 856 | 562 |
| 1 | 6.25 | 32 | 21 | 0 | 0 | 0 | 0 |
| Total | 99.15 | 555 | 369 | 555 | 369 | 30311 | 20188 |

Framing Check

Typical Floor Beam

I checked a typical floor beam on the 5th floor (current roof) spanning from Column G4 to Column H4. This area has a distributed dead load (DL) of 130 psf and a distributed live load (LL) of 150 psf.  TL = 1.2(DL) + 1.6(LL) = 396 psf. Assuming a simply supported span, Mu = 287 ft-k

The existing floor beam is a W16x26 with 14 shear studs along its length. Therefore, 7 stubs on each side transfer the shear for the max moment. Using Table 3-19 in the AISC Steel Construction Manual 13th Ed., I found that 7 studs per side do not satisfy the required calculated moment (øMp = 248 ft-k < 287 ft-k). Increasing the beam size to a W16x31 with the same number of stubs will yield a moment øMp = 300 ft-k. Adding additional shear studs to the original beam can also satisfy the moment capacity.

(See Appendix D for detailed calculations and assumptions)

Typical Floor Girder

The typical floor girder I checked is also part of the 5th floor framing spanning from Column H4 to Column H5. It too has a distributed dead load (DL) of 130 psf and a distributed live load (LL) of 150 psf.  TL = 1.2(DL) + 1.6(LL) = 396 psf. Assuming a simply supported span, Mu = 516 ft-k

The existing floor girder is a W18x35 with 26 shear studs along its length. With only 13 stubs per side acting to transfer the shear, Table 3-19 gives a moment of øMp = 445 ft-k < 516 ft-k. Increasing the beam size to a W18x46 with an equal number of studs will yield a moment of øMp = 542 ft-k. However, adding the additional shear studs to the smaller beam would be a more efficient and cost effective way to solve the problem.

(See Appendix E for detailed calculations and assumptions)

Typical Column Load

I checked column H4 to determine if it satisfied the strength requirements. A spreadsheet with the live load reduction factors and corresponding live loads can be found in Appendix F. Not all floor live loads can be reduced. The tributary area from each floor is approximately 556.5 sq. ft. acting on the column. I found a maximum of load P = 582 k acting on the column between the 3rd and 4th floor levels. The maximum load on the column is found at the first floor level where P = 759 k.

The column is spliced 4.5’ above the 3rd floor. A W14x74 extends from the 1st floor to the 3rd floor splice. From there, a W14x61 continues to the 5th floor level. In the future, a 3rd and potentially 4th column will extend to the top of the 8th floor (future roof framing). The minimum unbraced length for the W14x74 is 12.5’ occurring at the first floor. The minimum unbraced length for the W14x61 is 8.5’ acting on the 3rd floor above the column splice. The maximum unbraced length for each of the columns is 13.33’ at the other floors.

From Table 4-1 in the AISC Steel Manual, a W14x74 has a øPn = 750 k < 759 k. This number is close and probably considered acceptable because it is within 5% of the required value. If more strength is encouraged, a W14x82 has a øPn = 828 k.

For further column calculations and assumptions see Appendix G.

Typical Lateral Frame

The lateral moment frame I checked is part of Column line K, including columns K-2, K-4, and K-6. This frame is part of the exterior wall at the southeast corner of the building (see Figure 3 above). This frame is composed of W14x176 columns spliced 4.5 feet above the 3rd floor level and bear on spread footings below the 1st floor (assumed to be pinned at base support). Floor girders are W27x146 (32) at all upper floors and span 32’ from column face to face. Transverse beams frame into the girders at approximately the third points along their span.

I analyzed the frame by constructing a computer model of the frame in SAP. I assigned the existing beams and girders their corresponding structural properties. For the future floors, I assumed the new columns to be continuous from the 5th floor to the 8th floor. This assumption is acceptable because the analysis program is only computing the moments in the frame. Transverse beams are modeled as point loads on the girders at third points along their span. Transverse beams also frame into the columns, but are not considered in the model.

Seismic base shear (V=875k) is greater than the wind force and will control the lateral design. I assumed the central core area to handle the entire seismic load.

Since there is 4 framing elements acting in the same direction as Frame K, I assumed Frame K took ¼ of the seismic base shear and distributed it to each of the upper floors based on their ratio of weight and height in comparison to the entire structure.

(See Appendices B, C and H for detailed calculations and assumptions of lateral and gravity loads on Frame K.)

After running the SAP analysis program, I printed the girder and column moments and analyzed the data. The largest moment experienced by a column was Mu = 1106 ft-k at the center column

(K-4) on the underside of the 2nd floor. The

largest moment experienced by a girder was Mu = 1224 ft-k on the 2nd floor girder between column K-6 and K-4 (see Appendix H – page 30 for figure with moment diagram).

Using Table 3-2 in the AISC Steel Manual, a W14x176 has a øMp = 1200 ft-k which is greater than Mu = 1106 ft-k. Since all columns are W14x176, they all meet the required moment capacity. However, the column design moments decrease as they go up the building. Therefore, smaller columns could be used in place of the larger columns as long as they satisfy the required gravity and lateral loads.

For the girders, Table 3-19 in the AISC Steel Manual does not list W27x146 for composite action. Hand calculations for a W14x146 with shear studs in composite action can be found in Appendix I. Final calculations show the existing girders have a moment capacity øMn = 2152 ft-k > Mu = 1224 ft-k. Like the columns, the design moments slowly decrease as you move your way up the building. Therefore, smaller girders could possibly be used in the design of the upper floors (or future floors).

Appendix A

Typical and Alternate Beam to Column Moment Connections

Appendix B

Seismic Story Shear Forces

Appendix C

Wind Pressure Story Shear Forces

Appendix D

Spot Check calculations for a typical roof beam on the 5th floor (current roof/mechanical floor)

Appendix E

Spot Check calculations for a typical roof girder on the 5th floor (current roof/mechanical floor)

Appendix F

Live load reduction factors and corresponding column loads for a typical gravity column.

| Column H-4 |  |  |
| --- | --- | --- |
| Live Load Reduction |  |  |
| Level | AT | AI | Reducible | L.L. Red. (%) |
| 8 | 556.5 | 2226 | NO | 1.00 |
| 7 | 556.5 | 2226 | YES | 0.57 |
| 6 | 1113 | 4452 | YES | 0.47 |
| 5 | 556.5 | 2226 | NO | 1.00 |
| 4 | 1669.5 | 6678 | YES | 0.43 |
| 3 | 2226 | 8904 | YES | 0.41 |
| 2 | 2782.5 | 11130 | YES | 0.40 |
| 1 | 556.5 | 2226 | NO | 1.00 |
| Column H4 - Load Takedown |  |  |
| Level | L.L. (psf) | DL | Total Load(k) | Col. Load (k) |
| 8 | 25 | 80 | 75.7 |  |
| 7 | 80 | 90 | 100.6 | 75.7 |
| 6 | 80 | 90 | 93.9 | 176.2 |
| 5 | 150 | 130 | 220.4 | 270.2 |
| 4 | 80 | 90 | 91.0 | 490.5 |
| 3 | 80 | 90 | 89.2 | 581.5 |
| 2 | 80 | 90 | 88.6 | 670.8 |
| SOG |  |  | Total | 759.4 |

Appendix G

Spot Check calculations for a typical gravity column along its length

Appendix H

Simplified check of a lateral framing element: Moment Frame along Column Line K

SAP Computer Model output listing maximum moments along beam spans and column lengths

Sketch of Frame K with imposed point loads from transverse beams and lateral loads from seismic forces calculated in Appendix B.

Approximate calculation of concentrated framing loads from transverse beams framing into the Floor Girders at all levels along Frame K

Appendix I

Composite Moment capacity of floor girders along Frame K

# Text boxes

Column Frame K

Figure 4: Column Line – Frame K

Figure 5: Core Area