Mechanical Technical Report Two

McKinstry Oregon Headquarters

Alex Wyczalkowski 	October 24, 2008

Prepared for

Dr. Jelena Srebric, Ph.D.
Associate Professor of Architectural Engineering
The Pennsylvania State University

Table of Contents

1	Executive Summary	3

2	Building and Mechanical System Overview	4

3	Previous Energy Models	6

4	Energy Model Input	6

4.1	Input	6

4.2	Design Loads	7

5	Annual Energy Consumption	8

5.1	Airside Systems	8

5.2	Waterside Systems	8

5.3 	Energy Consumption	11

6	Annual Operating Costs	12

6.1	Utility Rate Analysis	12

6.2	Monthly and Annual Costs	12

6.3	Annual Cost Breakout	13

7	Discussion of Results	14

8	References	15

9	Appendix A – Design Document 	16

10	Appendix B – Portland Design Conditions	17

11	Appendix C – Load Calculation Printout	18

1	Executive Summary

McKinstry Oregon Headquarters is a 50,590 square foot, 2 story office building.  It began construction in March 2008 and is scheduled for completion in March 2009.  It is located in Northeast Portland, overlooking the Columbia River. The building contains 2 floors of offices, as well as a full kitchen, showers, and a small weight room for employees.  There is also a large warehouse at the west end of the building which is not ventilated.

The energy model in this report is the first such publication on McKinstry Oregon Headquarters.  Over the summer of 2008, Alexander Wyczalkowski worked for McKinstry in their Portland Office and created an energy model for the building.  The model used in this report is virtually the same exact model.

Design loads for the building are 18.03 BTU/(hr*sf) for cooling and 19.55 BTU/(hr*sf) for heating. Tables can be found in Section 4.2.  The most significant loads on the building are internal.  A lighting load of .81W/sf and equipment load of .5W/sf add both energy consumption as well as sensible heat to the building which needs to be cooled.  A population of 1 person/200sf adds latent and sensible load.  Exterior loads are also a factor, although the weather in Portland is generally mild, and only about 30% of the façade is glass.  A full description of loads and assumptions is located in Section 4.1.

Table 5.3.1 shows total electric consumption for the building to be 331,540 kWh per year. In addition, domestic hot water consumes 516 therms/year.  This produces an annual operating cost of $27,776.  Calculations can be found in Section 6.1.  Breaking down costs, the largest percent of costs comes from lighting loads and equipment loads.  This is caused by two factors, a mild climate, as well as an efficient building design. Cooling costs per square foot are 3.24¢ per year (see Table 6.3.1), and total energy costs per square foot are 54.9¢ per year (Table 6.3.2).  This is significantly lower than the average energy use for an office building, according to the ASHRAE Applications Handbook (see References).

2	Building and Mechanical System Overview

McKinstry Oregon Headquarters is a $15.5 million project which is scheduled for completion March 1, 2009.  This includes two buildings.  The only building of interest is the office building, as the other is simply a warehouse.  Costs for the 50,590 square foot office building total $11.1 million dollars.

Vestibule 484 sf

Office
23,000 sf
per floor

sf

4400

Ware

House

The headquarters is a 2 story office building.  The office is laid out in a simple rectangular grid.  At the West end of the building a full height 1 story warehouse attaches at a rotated angle.

N

Figure 2.1. Building Footprint

The flat, tilt-up concrete walls have vertical and horizontal lines to break the long straight façade. Approximately 30% of the office façade is glazing and windows are double glazed.  The base of the building is a reinforced concrete slab (there is no basement).  The exterior walls are backed by 3-5/8” metal studs and 3.5” batt insulation.  A built-up roof with 3” rigid insulation and 1.5” metal decking tops off the structure.  The roof also has several translucent skylights for natural day lighting.  The remaining lighting in the building is fairly standard with 100% fluorescent fixtures.

Figure 2.2. Waterside system, shown in heating mode. See Figure 5.2.1 for cooling mode (McKinstry Design Documents)

The central plant of the building is a heat recovery chiller that is used for both heating and cooling.  The mechanical system also includes an open loop ground source heat pump.  Ground water accepts heat from the condensing water in cooling mode and provides heat to the evaporator water in heating mode.  Evaporator side water and condenser side water are piped to the cooling and heating coils in the air handling unit, respectively.  A single rooftop AHU (with VFD) distributes air via ducts to the office section of the building.  Series VAV boxes with hot water reheats are located throughout the office.  Also, an airside economizer can provide cooling on light load days.  Two hot water unit heaters keep the warehouse warm in the winter.  Heating is provided by the hot water loop and there is no cooling or ventilation.  Linear diffusers condition the vestibule at the front of the building.  The electric room has a ductless split system ACU for additional cooling.

3	Previous Energy Models

During the summer of 2008, Alexander Wyczalkowski worked as an intern for McKinstry in their Portland office.  In August, he completed the energy model for McKinstry Oregon Headquarters.  This is the model that will be referenced throughout the report. There were no other energy models built by engineers at McKinstry.

4	Design Load Estimation

The following section is an overview of the inputs and assumptions put into the energy model for McKinstry Oregon Headquarters.  Any assumptions not listed, such as infiltration and hot water heater insulation, were left as defaults in the program, because specific information was not available for those parameters.

4.1 Input

Envelope

The energy model is comprised of 4 main areas or zones.  Generally the envelope of the building is the same in each area.

Table 4.1.1. eQUEST Envelope Assumptions

| SPACE | Floor to Floor Height | Floor to Ceiling Height | Roof Construction | Floor Construction | Wall Construction |
| --- | --- | --- | --- | --- | --- |
| Warehouse 4375 sf | 34.5’ | 34’ | Built up roof with 3” rigid insul above metal decking | 6” slab on grade | 7”concrete w/ 3.5” batt insul and metal studs |
| 1st Floor Office 23,715 sf | 14.5’ | 15’ | 2nd floor | 6” slab on grade with carpet | Same as warehouse |
| 2nd Floor Office 22,500 sf | 19.5’ | 19’ | Same as warehouse | 2” metal decking with 2.5” concrete topping | Same as warehouse |
| Atrium 484 sf | 14’ | 11’ | Same as warehouse | 6” slab on grade with carpet | Windows, double pane |

In addition, doors and windows are key parts of the envelope.  The following shows the assumptions used for openings.  Openings were placed on the computer model to match plans and elevations.

Table 4.1.2. Door and Window Assumptions

|  | Construction | Size |
| --- | --- | --- |
| Door – type 1 | Glass – double pane, Low-E | Most are 3’x8’ |
| Door – type 2 | Steel – insulated | Most are 3’x8’ |
| Door – type 3 | Steel – overhead, uninsulated | 10’x14’ |
| Windows | Glass – double pane, low-E | Most are 16’x8’ |
| Skylights | Acrylic, double pane, translucent, 4 total | 8’x15’ |

Loads and Existing Conditions

Table 4.1.3. Ventilation, Load Sources and Schedules:

|  | Value | Source |
| --- | --- | --- |
| OA Ventilation | 5,500 CFM | Mechanical Specs |
| People | 200sf/person | See Appendix A |
| Equipment | .5 W/sf* | See Appendix A |
| Lighting | .81 W/sf | See Appendix A |
| Design Conditions |  | See Appendix B |
| Schedule | Occupied hours: 6am-6pm, Mon-Fri; Unoccupied Sat,Sun, Holidays |  |

*equipment load is shown on the documents as being 1.1W/sf.  This was an overestimate to size the AHU.  After consulting with engineers, a more accurate estimate for energy consumption is .5W/sf

4.2 Design Loads

Table 4.2.1. Energy Model Loads vs Design Document Loads

|  | eQUEST model* | Design Documents |
| --- | --- | --- |
| Cooling Peak | 18.03 BTU/(hr*sf) | NA |
| sf/ton | 665.5 | 503 |
| Heating Peak | 19.55 BUT/(hr*sf) | NA |
| Supply Air at Peak Flow | .82 CFM/sf | NA |
| Min Outside Air/person | 33.88 CFM | 23.09 CFM |

*See Appendix C for eQUEST printout

5	Annual Energy Consumption

Once loads are found, HVAC systems need to be specified so that efficiencies can be estimated.  Section 2 of this report provides an overview of the mechanical systems in The McKinstry Oregon Headquarters.  All assumptions from Section 3 are used to find annual energy consumption.  See Table 4.1.3 for schedules.

5.1 Air Side Systems

There are two main air systems in the building.  The first is the main HVAC system, which is described in section 2 of this report.  In addition, the warehouse is heated by 2 hot water unit heaters.  There is no cooling or ventilation in the warehouse.

Table 5.1. Air Side System Assumptions

|  | Central HVAC (Office, Atrium) | Warehouse |
| --- | --- | --- |
| Cooling Source | Cooling Coils | None |
| Heating Source | Hot Water Coils | Hot Water Coils |
| System Type | Series VAV w/ Hot water Reheat | Forced Air HW Heaters |
| Return Air | Ducted | No ventilation |
| Occupied Setpoints | Cool: 74F, Heat: 70F | Same |
| Unoccupied Setpoints | Cool: 78F, Heat: 65F | Same |
| Supply Temps | Cool: 55F, Heat: 100F | Heat: 100F |
| Airflow | Minimum .17cfm/sf, 25%VAV | Minimum .17cfm/sf |
| Supply Fan | 46.2 BHP, Premium Efficiency, 37,220 CFM, 20.7% OA, VSD | .09 BHP Premium Efficiency |
| Return Fan | .91 BHP | NA |
| Economizer | Drybulb Temp, High Limit 55F | NA |

5.2 Water Side Systems

CHW Plant

The Chilled water plant in the building consists of 2 chillers.  The following are assumptions put into eQUEST for the CHW Plant.  Note that heat rejection is actually provided by a ground source heat exchanger.  eQUEST does not allow this option, so an efficient cooling tower must be assumed instead.

Chiller: Pump Config: Single system pump (1 total), variable flow

Head=81ft, flow=285 gpm
 Chiller size – 123.5 tons, type- hermetic scroll (assume screw)

Chiller efficiency – 70.6kw/123.5 tons= .5717 kw/ton

Cooling Tower: Head=90ft, flow= 130gpm
Control:	Load Reset, CHW Min=48F, CHW Max=58F, Demand Operation

Figure 5.2.1. Waterside System.  Shown in cooling mode. See Figure 2.2 for heating mode (McKinstry Design Documents)

HW Plant

Hot water for the heating coils comes from the condenser side of the 2 heat recovery chillers.  The ground water acts as the low temperature heat sink in the heat pump cycle as it warms the evaporator side refrigerant in the chiller. (see figure 2.2).  For the eQUEST model, the closest approximation to this system is a boiler with an efficiency equal to the COP of the heat pump.

Boiler: efficiency=410%, electric demand=94.3kW, output=1303 kBTUh

Loop Flow: variable, head=90ft, flow=130gpm
Control: Load Reset, HW Max=120F, HW Min=100F

DHW Equipment

Domestic Hot Water is entirely separate from the HVAC system.  It is heated by a gas furnace, the only natural gas used in the building. The following assumptions were put into eQUEST

Assumptions: Natural Gas Heater, storage, 95% efficient, 199 kBTUh, 100 gal tank, inlet=ground temp, 120F supply

Figure 5.2.2. eQUEST printout of Waterside System. Note discrepancy between actual system (Figure 5.2.1)

5.3 Energy Consumption

Figure 5.3.1. Electric consumption, gas consumption, and electricity breakdown

Table 5.3.1. Electric and gas consumption

=(Therms x10)

6	Annual Energy Costs

6.1 Utility Rate Analysis

Electricity is provided to the building by Portland General Electric (PGE).  The rate code is “PGE 83S 3P N-TOU Lrg N-Res Elec”.  Essentially this means it is large non-residential electric.  The following is a general formula for charges:

Monthly Charge = [$25 + $.05298*(kWh usage) + $2.27*(kW demand)]/.8

Where .8 is the Power Factor adjustment.

Natural Gas is provided by Northwest Natural.  The code is “NW Natural-OR 3-Comm Uniform”.  The following is a general formula for charges:

Monthly Charge = $8 + $1.198/therm

6.2 Monthly and Annual Costs

Figure 6.2.1. Monthly Energy Costs

6.3 Annual Cost Breakout

Table 6.3.1. Annual Cost Breakout.

|  | Yearly Energy Use (kWh) | Max Demand (kW) | Cost To Operate, annual ($)1 | Cost per square foot, annual (¢) |
| --- | --- | --- | --- | --- |
| Cooling | 15,210 | 40.3 | 1,497 | 3.242 |
| Heat Rejection | 9,600 | 11.5 | 797 | 1.732 |
| Space Heating | 41,790 | 101.4 | 4,014 | 7.93 |
| Ventilation&Fans | 51,860 | 29.6 | 4,151 | 8.20 |
| Pumps & Aux | 19,820 | 11.5 | 1,485 | 2.93 |
| Lighting | 118,780 | 35.8 | 9,029 | 17.85 |
| Misc Equip | 74,470 | 22.2 | 5,642 | 11.15 |
| Dom Hot Water | 51,590 (kBTU) | 20.14 (kBTU/h) | 714 | 1.41 |

1Cost to Operate = ∑Monthly Costs, Jan-Dec; see Excel File: Operating Costs.xlsx
2Square footage does not include Warehouse

The following table compares the usage breakdown of the eQUEST model, versus an average Office building. The percentages should approximately match between the two columns.  If they were significantly different, this could be a sign of an error in the energy model.

Table 6.3.2. Cost Breakdown. eQUEST model compared to ASHRAE*

|  | eQUEST Model, % of total cost | ASHRAE*, % of total usage |
| --- | --- | --- |
| Cooling | 5.48 | 9.36 |
| Heat Rejection | 2.92 |  |
| Space Heating | 14.7 | 25.0 |
| Ventilation&Fans | 15.2 | 5.34 |
| Pumps & Aux | 5.43 |  |
| Lighting | 33.0 | 28.9 |
| Misc Equip | 21.2 | 22.4 |
| Dom Hot Water | 2.06 | 8.95 |
| Total Cost per sf | $.549 | $1.51 |

*Energy End Use for Office Building, 1995 Commercial Building Energy Consumption (Applications Handbook)

7	Discussion of Results

Overall, McKinstry Oregon Headquarters is a fairly efficient building.  Although there are large internal loads in the building with lighting and equipment, the building is fairly well insulated and has an efficient mechanical system.

One key note to make about loads is the comparison between sf/ton.  In the design documents, sf/ton was 503.  In the eQUEST model, this value is 666.  These numbers are consistent with expectations because the design documents were over conservative to oversize the mechanical systems.  Another interesting comparison is minimum OA/person.  The design documents only spec 23 CFM, where as the energy model uses 34 CFM.

Utility Rates average to be about $.08 per kWh and $1.40 per therm.  These numbers are what should be expected for Oregon.  When breaking down monthly costs, bills are relatively flat, although peak slightly in the summer and winter months, as seen in figure 6.2.1.

Table 6.3.1 shows a yearly breakdown by usage type.  Most notably, cooling and heat rejection cost comes to 4.97 ¢ per sf annually.  Table 6.3.2 compares the usage breakdown of the eQUEST model, versus an average Office building.  The numbers are fairly similar.  Several discrepancies on the eQUEST model are lower cooling and heating percentages, as well as higher pump and miscellaneous operation.  The low cooling and heating loads could be due to the mild climate in Portland.  High pump loads could be due to the ground source heat pump, which has to pump water from several hundred feet underground.

8	References

ASHRAE. 2005, ANSI/ASHRAE, Portland Design Conditions.  American Society of Heating Refrigeration and Air Conditioning Engineers, Inc., Atlanta, GA. 2007

ASHRAE. 2003. ASHRAE Handbook, HVAC Applications. Section 35.8, Table 2A. American Society of Heating Refrigeration and Air Conditioning Engineers, Inc., Atlanta, GA. 2003

McKinstry. 2008. Design Documents. McKinstry, Seattle, WA. 2008

Wozniak, Aaron. 2008. Personal Communication. Portland, OR. 2008

9	Appendix A – Design Document

10	Appendix B – Ventilation Rate Calculations

11	Appendix C – Load Calculation Printout