## Slide 1
Nate Mooney | Mechanical Option
Advisor: William P. Bahnfleth, PH.D., PE
The Pennsylvania State University
Architectural Engineering
Spring 2013
75 Ames Street:
Cambridge, Massachusetts
INTRODUCTION
DEPTH I
DEPTH II
DEPTH III
BREADTH I
CONCLUSION
ACKNOWLEDGEMENTS
QUESTIONS

## Slide 2
[COST] $188,000,000 Building Cost
[CONSTRUCTION] January 2012  Early 2014
[LOCATION] 75 Ames Street, Cambridge Massachusetts
The Broad Institute Expansion
75 Ames Street:
Nathaniel Mooney
[SIZE] 250,000 SF
[LEVELS] 15 STORYS
GROUND FLOOR – RETAIL
L-11 – MIXED OFFICES & LABS
L-12 – VIVARIUM
3 MECHANICAL LEVELS M1,M2 & M3
[OCCUPANCY] Mixed Assembly
Restaurant | A-2
Large Conference & Meeting Rooms | A-3
Small Conference & Offices | B
Retail Tenant | M
Laboratory | H-2, H-3, H-4 High Hazard
INTRODUCTION
Building Overview
Existing Mechanical
DEPTH I
DEPTH II
DEPTH III
BREADTH I
CONCLUSION
ACKNOWLEDGEMENTS
QUESTIONS
BUILDING OVERVIEW

## Slide 3
[COST] $188,000,000 Building Cost
[CONSTRUCTION] January 2012  Early 2014
[LOCATION] 75 Ames Street, Cambridge Massachusetts
The Broad Institute Expansion
[SIZE] 250,000 SF
[LEVELS] 15 STORYS
GROUND FLOOR – RETAIL
L-11 – MIXED OFFICES & LABS
L-12 – VIVARIUM
3 MECHANICAL LEVELS M1,M2 & M3
[OCCUPANCY] Mixed Assembly
Restaurant | A-2
Large Conference & Meeting Rooms | A-3
Small Conference & Offices | B
Retail Tenant | M
Laboratory | H-2, H-3, H-4 High Hazard
INTRODUCTION
Building Overview
Existing Mechanical
DEPTH I
DEPTH II
DEPTH III
BREADTH I
CONCLUSION
ACKNOWLEDGEMENTS
QUESTIONS
75 Ames Street:
Nathaniel Mooney
BUILDING OVERVIEW

## Slide 4
[COST] $188,000,000 Building Cost
[CONSTRUCTION] January 2012  Early 2014
[LOCATION] 75 Ames Street, Cambridge Massachusetts
The Broad Institute Expansion
[SIZE] 250,000 SF
[LEVELS] 15 STORYS
GROUND FLOOR – RETAIL
L-11 – MIXED OFFICES & LABS
L-12 – VIVARIUM
3 MECHANICAL LEVELS M1,M2 & M3
[OCCUPANCY] Mixed Assembly
Restaurant | A-2
Large Conference & Meeting Rooms | A-3
Small Conference & Offices | B
Retail Tenant | M
Laboratory | H-2, H-3, H-4 High Hazard
INTRODUCTION
Building Overview
Existing Mechanical
DEPTH I
DEPTH II
DEPTH III
BREADTH I
CONCLUSION
ACKNOWLEDGEMENTS
QUESTIONS
75 Ames Street:
Nathaniel Mooney
BUILDING OVERVIEW

## Slide 5
[COST] $188,000,000 Building Cost
[CONSTRUCTION] January 2012  Early 2014
[LOCATION] 75 Ames Street, Cambridge Massachusetts
The Broad Institute Expansion
Frank Gehry – Ray & Maria Center at MIT
[SIZE] 250,000 SF
[LEVELS] 15 STORYS
GROUND FLOOR – RETAIL
L-11 – MIXED OFFICES & LABS
L-12 – VIVARIUM
3 MECHANICAL LEVELS M1,M2 & M3
[OCCUPANCY] Mixed Assembly
Restaurant | A-2
Large Conference & Meeting Rooms | A-3
Small Conference & Offices | B
Retail Tenant | M
Laboratory | H-2, H-3, H-4 High Hazard
INTRODUCTION
Building Overview
Existing Mechanical
DEPTH I
DEPTH II
DEPTH III
BREADTH I
CONCLUSION
ACKNOWLEDGEMENTS
QUESTIONS
75 Ames Street:
Nathaniel Mooney
BUILDING OVERVIEW

## Slide 6
Existing Mechanical System
[AIR SIDE]
    100% Outside Air
      4 – Ganged 115,000 CFM AHU’s
          Basement  L-11
      1 – 60,000 CFM AHU
          Vivarium L-12
      2 – 230,000 CFM EAHU
      VAV Box with terminal reheat
Exhaust Air Handling Units
Air Handling Units
The Broad Institute Expansion
INTRODUCTION
Building Overview
Existing Mechanical
DEPTH I
DEPTH II
DEPTH III
BREADTH I
CONCLUSION
ACKNOWLEDGEMENTS
QUESTIONS
75 Ames Street:
Nathaniel Mooney

## Slide 7
[WATER SIDE]
Heating Plant
        2 - 500 BHP Preheat fire-tube Boilers
          AHU 1,2,3,4,5 preheat
          HVU’s
        4 – 120 BHP Reheat Condensing Boilers
          Building terminal reheat
        2 – 215 BHP MPS Boilers
          60 PSIG
          Humidification
          Process steam loads
The Broad Institute Expansion
Existing Mechanical System
INTRODUCTION
Building Overview
Existing Mechanical
DEPTH I
DEPTH II
DEPTH III
BREADTH I
CONCLUSION
ACKNOWLEDGEMENTS
QUESTIONS
75 Ames Street:
Nathaniel Mooney

## Slide 8
[WATER SIDE]
Chiller Plant
      42 °F water
        3 – 1000 ton centrifugal chillers
          3 – 1000 ton cooling towers on VFD
          AHU 1,2,3 & 4 cooling
        2 – 450 ton centrifugal chillers
          2 – 450 ton cooling towers on VFD
          AHU 5
          Process chilled water loads
The Broad Institute Expansion
INTRODUCTION
Building Overview
Existing Mechanical
DEPTH I
DEPTH II
DEPTH III
BREADTH I
CONCLUSION
ACKNOWLEDGEMENTS
QUESTIONS
Existing Mechanical System
75 Ames Street:
Nathaniel Mooney

## Slide 9
The Broad Institute Expansion
INTRODUCTION
DEPTH I
GOAL
OPERATION
RESULTS
COST & SAVINGS
EMISSIONS
DEPTH II
DEPTH III
BREADTH I
CONCLUSION
ACKNOWLEDGEMENTS
QUESTIONS
[GOAL]
Turn down ventilation air in order to save energy while maintaining appropriate room conditions.
Demand Controlled Ventilation with Aircuity’s Optinet System
75 Ames Street:
Nathaniel Mooney

## Slide 10
The Broad Institute Expansion
[HOW IT WORKS]
Typical lab rooms are supplied with 6/12ACH
Aircuity allows air change rates of 2/4ACH
    15-20 rooms every 15 minutes
        Photoionization ~ Ammonia
        Metal Oxide detector
        Lasers
        CO2 Sensors
        Dew point
    Dilution ventilation up to 15 ACH
        Labs clean of contaminants 99% of time
INTRODUCTION
DEPTH I
GOAL
OPERATION
RESULTS
COST & SAVINGS
EMISSIONS
DEPTH II
DEPTH III
BREADTH I
CONCLUSION
ACKNOWLEDGEMENTS
QUESTIONS
Demand Controlled Ventilation with Aircuity’s Optinet System
75 Ames Street:
Nathaniel Mooney

## Slide 11
The Broad Institute Expansion
[RESULTS]
Using Trane TRACE 700 and the new ventilation rates of 2/4 ACH for a group of 32 select lab rooms
 | Electricity (KWH) | Natural Gas (Therms) | Electricity Cost Per Year | Natural Gas Cost Per Year | Total Cost Per Year
Original System | 9985524.00 | 107047.00 | $ 2,007090.32 | $ 170,954.06 | $ 2,178,044.38
DCV | 9,059,513.00 | 105,222.00 | $ 1,820,962.11 | $ 168,039.53 | $ 1,989,001.65
Difference | 926,011.00 | 1,825.00 | $ 186,128.21 | $ 2,914.53 | $ 189,042.74
 |  |  |  | % Change | -9%
Energy Usage |  | Original System VAV Reheat |  | Alternate DCV | 
 |  | Electric KWH | Gas Therms | Electric KWH | Gas Therms
 | Jan | 721,666 | 17,302 | 630,014 | 18,918
 | Feb | 654,882 | 16,453 | 571,874 | 18,323
 | Mar | 791,432 | 10,610 | 694,572 | 10,289
 | Apr | 746,783 | 6,680 | 659,139 | 4,954
 | May | 894,909 | 6,230 | 811,156 | 4,473
 | June | 978,922 | 4,318 | 923,273 | 3,839
 | July | 962,894 | 1,243 | 947,253 | 3,007
 | Aug | 1,040,655 | 3,556 | 987,417 | 3,922
 | Sept | 847,768 | 6,004 | 766,895 | 4,229
 | Oct | 895,855 | 7,054 | 800,672 | 4,943
 | Nov | 771,446 | 8,173 | 664,497 | 6,118
 | Dec | 678,311 | 19,423 | 602,751 | 22,206
 | Total | 9,985,524 | 107,047 | 9,059,513 | 105,222
 |  |  | Difference |  | 
 |  |  | Electrical KWH | Gas Therms | 
 |  |  | -926,011 | -1,825 | 
Demand Controlled Ventilation with Aircuity’s Optinet System
INTRODUCTION
DEPTH I
GOAL
OPERATION
RESULTS
COST & SAVINGS
EMISSIONS
DEPTH II
DEPTH III
BREADTH I
CONCLUSION
ACKNOWLEDGEMENTS
QUESTIONS
75 Ames Street:
Nathaniel Mooney

## Slide 12
The Broad Institute Expansion
[RESULTS]
Using Trane TRACE 700 and the new ventilation rates of 2/4 ACH for a group of 32 select lab rooms
 | Electricity (KWH) | Natural Gas (Therms) | Electricity Cost Per Year | Natural Gas Cost Per Year | Total Cost Per Year
Original System | 9985524.00 | 107047.00 | $ 2,007090.32 | $ 170,954.06 | $ 2,178,044.38
DCV | 9,059,513.00 | 105,222.00 | $ 1,820,962.11 | $ 168,039.53 | $ 1,989,001.65
Difference | 926,011.00 | 1,825.00 | $ 186,128.21 | $ 2,914.53 | $ 189,042.74
 |  |  |  | % Change | -9%
Demand Controlled Ventilation with Aircuity’s Optinet System
INTRODUCTION
DEPTH I
GOAL
OPERATION
RESULTS
COST & SAVINGS
EMISSIONS
DEPTH II
DEPTH III
BREADTH I
CONCLUSION
ACKNOWLEDGEMENTS
QUESTIONS
Chart: Original VAV Vs. Aircuity Electricity Usage
| Jan | Feb | Mar | Apr | May | June | July | Aug | Sept | Oct | Nov | Dec
Original System VAV Reheat | 721666 | 654882 | 791432 | 746783 | 894909 | 978922 | 962894 | 1040655 | 847768 | 895855 | 771446 | 678311
Alternate DCV | 630014 | 571874 | 694572 | 659139 | 811156 | 923273 | 947253 | 987417 | 766895 | 800672 | 664497 | 602751
75 Ames Street:
Nathaniel Mooney

## Slide 13
The Broad Institute Expansion
[RESULTS]
Using Trane TRACE 700 and the new ventilation rates of 2/4 ACH for a group of 32 select lab rooms
 | Electricity (KWH) | Natural Gas (Therms) | Electricity Cost Per Year | Natural Gas Cost Per Year | Total Cost Per Year
Original System | 9985524.00 | 107047.00 | $ 2,007090.32 | $ 170,954.06 | $ 2,178,044.38
DCV | 9,059,513.00 | 105,222.00 | $ 1,820,962.11 | $ 168,039.53 | $ 1,989,001.65
Difference | 926,011.00 | 1,825.00 | $ 186,128.21 | $ 2,914.53 | $ 189,042.74
 |  |  |  | % Change | -9%
INTRODUCTION
DEPTH I
GOAL
OPERATION
RESULTS
COST & SAVINGS
EMISSIONS
DEPTH II
DEPTH III
BREADTH I
CONCLUSION
ACKNOWLEDGEMENTS
QUESTIONS
Demand Controlled Ventilation with Aircuity’s Optinet System
Chart: Original VAV Vs. Aircuity Gas Consumption
| Jan | Feb | Mar | Apr | May | June | July | Aug | Sept | Oct | Nov | Dec
Original System VAV Reheat | 17302 | 16453 | 10610 | 6680 | 6230 | 4318 | 1243 | 3556 | 6004 | 7054 | 8173 | 19423
Alternate DCV | 18918 | 18323 | 10289 | 4954 | 4473 | 3839 | 3007 | 3922 | 4229 | 4943 | 6118 | 22206
75 Ames Street:
Nathaniel Mooney

## Slide 14
The Broad Institute Expansion
Demand Controlled Ventilation with Aircuity’s Optinet System
[COSTS & SAVINGS]
First Cost Estimate:
      Typically budgeted at $5,000 per space
      32 spaces
      $160,000
      Optional:
        $20,963 / Year Maintenance
        1st year waived
Payback
      Annual savings = 189,042.74
      0.85 Year payback
INTRODUCTION
DEPTH I
GOAL
OPERATION
RESULTS
COST & SAVINGS
EMISSIONS
DEPTH II
DEPTH III
BREADTH I
CONCLUSION
ACKNOWLEDGEMENTS
QUESTIONS
2.5% Inflation |  |  |  |  | 
10 Year Life Cycle Cost Analysis |  |  |  |  | 
YEAR | Original System VAV Reheat | DCV - Aircuity Alternate | Savings | With Maintanance First Year Free | Savings
0 | $- | $160,000.00 | $(160,000.00) | $160,000.00 | $(160,000.00)
1 | $2,123,593.27 | $2,095,276.61 | $28,316.67 | $2,095,276.61 | $28,316.67
2 | $4,141,006.88 | $3,933,689.38 | $207,317.50 | $3,953,617.33 | $187,389.55
3 | $6,056,222.57 | $5,678,871.97 | $377,350.60 | $5,717,731.48 | $338,491.09
4 | $7,873,089.34 | $7,334,336.87 | $538,752.46 | $7,391,168.90 | $481,920.44
5 | $9,595,327.63 | $8,903,479.24 | $691,848.39 | $8,977,360.87 | $617,966.76
6 | $11,226,533.33 | $10,389,580.52 | $836,952.80 | $10,479,623.77 | $746,909.56
7 | $12,770,181.66 | $11,795,812.07 | $974,369.59 | $11,901,162.66 | $869,018.99
8 | $14,229,630.99 | $13,125,238.55 | $1,104,392.44 | $13,245,074.85 | $984,556.14
9 | $15,608,126.49 | $14,380,821.32 | $1,227,305.17 | $14,514,353.20 | $1,093,773.29
10 | $16,908,803.70 | $15,565,421.68 | $1,343,382.02 | $15,711,889.46 | $1,196,914.24
75 Ames Street:
Nathaniel Mooney

## Slide 15
The Broad Institute Expansion
[EMISSIONS]
INTRODUCTION
DEPTH I
GOAL
OPERATION
RESULTS
COST & SAVINGS
EMISSIONS
DEPTH II
DEPTH III
BREADTH I
CONCLUSION
ACKNOWLEDGEMENTS
QUESTIONS
ENVIRONMENTAL IMPACT |  |  |  |  | 
 | Unit | Original System VAV Reheat | DCV - Aircuity Alternate | % Change | Difference
CO2 | lbm/yr | 876,396,480 | 795,123,520 | -9.27% | 81,272,960
SO2 | gm/yr | 2,742,078 | 2,487,791 | -9.27% | 254,287
NOX | gm/yr | 742,165 | 673,340 | -9.27% | 68,825
75 Ames Street:
Nathaniel Mooney
Demand Controlled Ventilation with Aircuity’s Optinet System

## Slide 16
The Broad Institute Expansion
Chilled Beams Alternate
[GOAL]
To reduce energy consumption and carbon footprint compared to the original system by lowing supply air rates and need for reheat.
INTRODUCTION
DEPTH I
DEPTH II
GOAL
OPERATION
RESULTS
COST & SAVINGS
EMISSIONS
DEPTH III
BREADTH I
CONCLUSION
ACKNOWLEDGEMENTS
QUESTIONS
75 Ames Street:
Nathaniel Mooney

## Slide 17
The Broad Institute Expansion
Chilled Beams Alternate
[OPERATION]
  Determine Sensible and Latent Loads for Space
      TRANE TRACE 700
  Air Flow Rate For Space
      Vbz= Rp * Pz + Ra * Az
      Office 5 cfm / person & .06 cfm/ft2
      Lab 10 cfm / person & 18 cfm/ft2
  Cooling Capacity of Air
      Humidity Ratio wsupply= 0.007997 lbw/lbDA
  wroom = 0.009233 lbw/lbDA
      Qlatent = 4840 Vbz (wroom – wsupply)
INTRODUCTION
DEPTH I
DEPTH II
GOAL
OPERATION
RESULTS
COST & SAVINGS
EMISSIONS
DEPTH III
BREADTH I
CONCLUSION
ACKNOWLEDGEMENTS
QUESTIONS
  4) Required Supply Air To Remove Latent
      Qlatent = 4840 Vbz_new (wroom- wsupply)
      This gives a new sensible capacity of
Qsensible= 1.08 Vbz_new (Troom- Tsupply)
  5) Sensible Load for Chilled Beams
      Sensible load from Trace minus Qsens above
  6) Size & Quantity
      From PRICE-HVAC catalogue
75 Ames Street:
Nathaniel Mooney

## Slide 18
Unit | Type | Quantity | CFM | Min SP | HP | RPM
EXISTING |  |  |  |  |  | 
AHU1 | plenum | 4 | 28750 | 7.5 | 75 | 1750
AHU2 | plenum | 4 | 28750 | 7.5 | 75 | 1750
AHU3 | plenum | 4 | 28750 | 7.5 | 75 | 1750
AHU4 | plenum | 4 | 28750 | 7.5 | 75 | 1750
AHU5 | plenum | 4 | 15000 | 7.5 | 50 | 1750
EAHU1 | Cent. | 5 | 57,500 | 5.3 | 100 | 770
EAHU2 | Cent. | 5 | 57,500 | 5.3 | 100 | 770
EAHU3 | Cent. | 3 | 30000 | 4.5 | 50 | 1132
REDESIGN |  |  |  |  |  | 
AHU1 | plenum | 4 | 30516 | 7.5 | 89.76 | 1858
AHU2 | plenum | 4 | 30516 | 7.5 | 89.76 | 1858
AHU3 | plenum | 4 | 30516 | 7.5 | 89.76 | 1858
AHU5 | plenum | 4 | 15000 | 7.5 | 50 | 1750
EAHU1 | Cent. | 5 | 45,774 | 5.3 | 50.46 | 613
EAHU2 | Cent. | 5 | 45,774 | 5.3 | 50.46 | 613
EAHU3 | Cent. | 3 | 30000 | 4.5 | 50 | 1132
The Broad Institute Expansion
Chilled Beams Alternate
[RESULTS]
INTRODUCTION
DEPTH I
DEPTH II
GOAL
OPERATION
RESULTS
COST & SAVINGS
EMISSIONS
DEPTH III
BREADTH I
CONCLUSION
ACKNOWLEDGEMENTS
QUESTIONS
EXISTING |  |  | 
AHU-1-2 | VAV | 77,274 | 26,333
AHU-3-4 | VAV | 223,882 | 121,876
REDESIGN |  |  | 
AHU-1-2 | VAV | 77,274 | 26,333
% CHANGE |  | 0% | 0%
AHU-3-4 | ACTIVE CHILLED BEAMS | 82,552 | 82,552
% CHANGE |  | -63% | -32%
Unit | Fan Type | # Fans | Original | Redesign
AHU1 | plenum | 4 | 28750 | 30516
AHU2 | plenum | 4 | 28750 | 30516
AHU3 | plenum | 4 | 28750 | 30516
AHU4 | plenum | 4 | 28750 | ELIMINATED
AHU5 | plenum | 4 | 15000 | 15000
EAHU1 | Cent. | 5 | 57,500 | 45,774
EAHU2 | Cent. | 5 | 57,500 | 45,774
EAHU3 | Cent. | 3 | 30000 | 30000
75 Ames Street:
Nathaniel Mooney

## Slide 19
The Broad Institute Expansion
Chilled Beams Alternate
[RESULTS]
INTRODUCTION
DEPTH I
DEPTH II
GOAL
OPERATION
RESULTS
COST & SAVINGS
EMISSIONS
DEPTH III
BREADTH I
CONCLUSION
ACKNOWLEDGEMENTS
QUESTIONS
 | Electricity (kWh) | Natural Gas (Therms) | Electricity Cost Per year | Natural Gas Cost per year | Total Cost Per Year
Original System | 9,985,524.00 | 107,047.00 | $2,007,090.32 | $170,954.06 | $2,178,044.38
Chilled Beams | 7,817,379.00 | 46,671.00 | $1,571,293.18 | $74,533.59 | $1,645,826.77
Difference | 2,168,145.00 | 60,376.00 | $435,797.15 | $96,420.47 | $532,217.62
 |  |  |  | % change | -24%
Utility | Unit | Cost
Electricity | $/KWH | 0.201
Natural Gas | $/Therm | 1.597
Energy Usage | System | Original System VAV Reheat |  | Alternate Chilled Beams |  | 
 | Units | Electric KWH | Gas Therms | Electric KWH | Gas Therms | 
 | Jan | 721,666 | 17,302 | 577,161 | 9,233 | 
 | Feb | 654,882 | 16,453 | 522,319 | 8,833 | 
 | Mar | 791,432 | 10,610 | 630,116 | 4,829 | 
 | Apr | 746,783 | 6,680 | 582,533 | 2,293 | 
 | May | 894,909 | 6,230 | 696,508 | 1,635 | 
 | June | 978,922 | 4,318 | 753,254 | 1,097 | 
 | July | 962,894 | 1,243 | 749,789 | 374 | 
 | Aug | 1,040,655 | 3,556 | 799,291 | 949 | 
 | Sept | 847,768 | 6,004 | 661,653 | 1,606 | 
 | Oct | 895,855 | 7,054 | 692,335 | 1,936 | 
 | Nov | 771,446 | 8,173 | 601,660 | 3,106 | 
 | Dec | 678,311 | 19,423 | 550,762 | 10,781 | 
 | Total | 9,985,524 | 107,047 | 7,817,379 | 46,671 | 
 |  |  |  | Difference |  | 
 |  |  |  | Electrical KWH |  | Gas Therms
 |  |  |  | -2,168,145 |  | -60,376
EXISTING |  |  | 
AHU-1-2 | VAV | 77,274 | 26,333
AHU-3-4 | VAV | 223,882 | 121,876
REDESIGN |  |  | 
AHU-1-2 | VAV | 77,274 | 26,333
% CHANGE |  | 0% | 0%
AHU-3-4 | ACTIVE CHILLED BEAMS | 82,552 | 82,552
% CHANGE |  | -63% | -32%
AHU Redesign |  |  |  | 
Unit | Fan Type | # Fans | Original | Redesign
AHU1 | plenum | 4 | 28750 | 30516
AHU2 | plenum | 4 | 28750 | 30516
AHU3 | plenum | 4 | 28750 | 30516
AHU4 | plenum | 4 | 28750 | ELIMINATED
AHU5 | plenum | 4 | 15000 | 15000
EAHU1 | Cent. | 5 | 57,500 | 45,774
EAHU2 | Cent. | 5 | 57,500 | 45,774
EAHU3 | Cent. | 3 | 30000 | 30000
Fan Sizing |  |  |  |  |  | 
Unit | Type | Quantity | CFM | Min SP | HP | RPM
EXISTING |  |  |  |  |  | 
AHU1 | plenum | 4 | 28750 | 7.5 | 75 | 1750
AHU2 | plenum | 4 | 28750 | 7.5 | 75 | 1750
AHU3 | plenum | 4 | 28750 | 7.5 | 75 | 1750
AHU4 | plenum | 4 | 28750 | 7.5 | 75 | 1750
AHU5 | plenum | 4 | 15000 | 7.5 | 50 | 1750
EAHU1 | Cent. | 5 | 57,500 | 5.3 | 100 | 770
EAHU2 | Cent. | 5 | 57,500 | 5.3 | 100 | 770
EAHU3 | Cent. | 3 | 30000 | 4.5 | 50 | 1132
REDESIGN |  |  |  |  |  | 
Unit | Type | Quantity | CFM | Min SP | HP | RPM
AHU1 | plenum | 4 | 30516 | 7.5 | 89.76 | 1858
AHU2 | plenum | 4 | 30516 | 7.5 | 89.76 | 1858
AHU3 | plenum | 4 | 30516 | 7.5 | 89.76 | 1858
AHU5 | plenum | 4 | 15000 | 7.5 | 50 | 1750
EAHU1 | Cent. | 5 | 45,774 | 5.3 | 50.46 | 613
EAHU2 | Cent. | 5 | 45,774 | 5.3 | 50.46 | 613
EAHU3 | Cent. | 3 | 30000 | 4.5 | 50 | 1132
Chart: Original VAV System VS. Chilled Beams Electricity
| Jan | Feb | Mar | Apr | May | June | July | Aug | Sept | Oct | Nov | Dec
Original System VAV Reheat | 721666 | 654882 | 791432 | 746783 | 894909 | 978922 | 962894 | 1040655 | 847768 | 895855 | 771446 | 678311
Alternate Chilled Beams | 577161 | 522319 | 630116 | 582533 | 696508 | 753254 | 749789 | 799291 | 661653 | 692335 | 601660 | 550762
75 Ames Street:
Nathaniel Mooney

## Slide 20
The Broad Institute Expansion
Chilled Beams Alternate
[RESULTS]
INTRODUCTION
DEPTH I
DEPTH II
GOAL
OPERATION
RESULTS
COST & SAVINGS
EMISSIONS
DEPTH III
BREADTH I
CONCLUSION
ACKNOWLEDGEMENTS
QUESTIONS
 | Electricity (kWh) | Natural Gas (Therms) | Electricity Cost Per year | Natural Gas Cost per year | Total Cost Per Year
Original System | 9,985,524.00 | 107,047.00 | $2,007,090.32 | $170,954.06 | $2,178,044.38
Chilled Beams | 7,817,379.00 | 46,671.00 | $1,571,293.18 | $74,533.59 | $1,645,826.77
Difference | 2,168,145.00 | 60,376.00 | $435,797.15 | $96,420.47 | $532,217.62
 |  |  |  | % change | -24%
Utility | Unit | Cost
Electricity | $/KWH | 0.201
Natural Gas | $/Therm | 1.597
EXISTING |  |  | 
AHU-1-2 | VAV | 77,274 | 26,333
AHU-3-4 | VAV | 223,882 | 121,876
REDESIGN |  |  | 
AHU-1-2 | VAV | 77,274 | 26,333
% CHANGE |  | 0% | 0%
AHU-3-4 | ACTIVE CHILLED BEAMS | 82,552 | 82,552
% CHANGE |  | -63% | -32%
AHU Redesign |  |  |  | 
Unit | Fan Type | # Fans | Original | Redesign
AHU1 | plenum | 4 | 28750 | 30516
AHU2 | plenum | 4 | 28750 | 30516
AHU3 | plenum | 4 | 28750 | 30516
AHU4 | plenum | 4 | 28750 | ELIMINATED
AHU5 | plenum | 4 | 15000 | 15000
EAHU1 | Cent. | 5 | 57,500 | 45,774
EAHU2 | Cent. | 5 | 57,500 | 45,774
EAHU3 | Cent. | 3 | 30000 | 30000
Fan Sizing |  |  |  |  |  | 
Unit | Type | Quantity | CFM | Min SP | HP | RPM
EXISTING |  |  |  |  |  | 
AHU1 | plenum | 4 | 28750 | 7.5 | 75 | 1750
AHU2 | plenum | 4 | 28750 | 7.5 | 75 | 1750
AHU3 | plenum | 4 | 28750 | 7.5 | 75 | 1750
AHU4 | plenum | 4 | 28750 | 7.5 | 75 | 1750
AHU5 | plenum | 4 | 15000 | 7.5 | 50 | 1750
EAHU1 | Cent. | 5 | 57,500 | 5.3 | 100 | 770
EAHU2 | Cent. | 5 | 57,500 | 5.3 | 100 | 770
EAHU3 | Cent. | 3 | 30000 | 4.5 | 50 | 1132
REDESIGN |  |  |  |  |  | 
Unit | Type | Quantity | CFM | Min SP | HP | RPM
AHU1 | plenum | 4 | 30516 | 7.5 | 89.76 | 1858
AHU2 | plenum | 4 | 30516 | 7.5 | 89.76 | 1858
AHU3 | plenum | 4 | 30516 | 7.5 | 89.76 | 1858
AHU5 | plenum | 4 | 15000 | 7.5 | 50 | 1750
EAHU1 | Cent. | 5 | 45,774 | 5.3 | 50.46 | 613
EAHU2 | Cent. | 5 | 45,774 | 5.3 | 50.46 | 613
EAHU3 | Cent. | 3 | 30000 | 4.5 | 50 | 1132
Chart: Original VAV System VS. Chilled Beams Electricity
| Jan | Feb | Mar | Apr | May | June | July | Aug | Sept | Oct | Nov | Dec
Original System VAV Reheat | 721666 | 654882 | 791432 | 746783 | 894909 | 978922 | 962894 | 1040655 | 847768 | 895855 | 771446 | 678311
Alternate Chilled Beams | 577161 | 522319 | 630116 | 582533 | 696508 | 753254 | 749789 | 799291 | 661653 | 692335 | 601660 | 550762
Chart: Original VAV System Vs. Chilled Beams Heating
| Jan | Feb | Mar | Apr | May | June | July | Aug | Sept | Oct | Nov | Dec
Original System VAV Reheat | 17302 | 16453 | 10610 | 6680 | 6230 | 4318 | 1243 | 3556 | 6004 | 7054 | 8173 | 19423
Alternate Chilled Beams | 9233 | 8833 | 4829 | 2293 | 1635 | 1097 | 374 | 949 | 1606 | 1936 | 3106 | 10781
75 Ames Street:
Nathaniel Mooney

## Slide 21
The Broad Institute Expansion
Chilled Beams Alternate
[COST & SAVINGS]
  Chilled Beams $130/LF
  VAV box’s priced on CFM
  Pipe priced at $50 LF
  CHWP From RS Means
  1.4 years payback
W/ 2.5% inflation |  |  | 
10 Year Life Cycle Cost Analysis |  |  | 
YEAR | Original System VAV Reheat | Chilled Beams Alternate | Savings
0 | $- | $743,167.79 | $(743,167.79)
1 | $2,123,593.27 | $2,329,269.69 | $(205,676.42)
2 | $4,141,006.89 | $3,835,602.02 | $305,404.87
3 | $6,056,222.57 | $5,265,161.94 | $791,060.63
4 | $7,873,089.33 | $6,620,846.61 | $1,252,242.73
5 | $9,595,327.63 | $7,905,456.32 | $1,689,871.31
6 | $11,226,533.33 | $9,121,697.51 | $2,104,835.81
7 | $12,770,181.66 | $10,272,185.74 | $2,497,995.92
8 | $14,229,630.99 | $11,359,448.49 | $2,870,182.49
9 | $15,608,126.50 | $12,385,927.99 | $3,222,198.50
10 | $16,908,803.70 | $13,353,983.86 | $3,554,819.84
INTRODUCTION
DEPTH I
DEPTH II
GOAL
OPERATION
RESULTS
COST & SAVINGS
EMISSIONS
DEPTH III
BREADTH I
CONCLUSION
ACKNOWLEDGEMENTS
QUESTIONS
Unit | Cost
Chilled Beams & Resized VAV Box's Total | $962,824.69
VAV BOX & Diffusers | ($417,784.28)
Piping | $822,942.38
AHU Removal | ($640,815.00)
CHW PUMP | $16,000.00
Total Cost | $743,167.79
75 Ames Street:
Nathaniel Mooney

## Slide 22
The Broad Institute Expansion
Chilled Beams Alternate
[EMISSIONS]
INTRODUCTION
DEPTH I
DEPTH II
GOAL
OPERATION
RESULTS
COST & SAVINGS
EMISSIONS
DEPTH III
BREADTH I
CONCLUSION
ACKNOWLEDGEMENTS
QUESTIONS
ENVIRONMENTAL IMPACT |  |  |  |  | 
 | Unit | Original System VAV Reheat | Chilled Beams Alternate | % Change | Difference
CO2 | lbm/yr | 876,396,480 | 685,284,352 | -21.81% | 191,112,128
SO2 | gm/yr | 2,742,078 | 2,144,125 | -21.81% | 597,953
NOX | gm/yr | 742,165 | 580,324 | -21.81% | 161,841
75 Ames Street:
Nathaniel Mooney

## Slide 23
The Broad Institute Expansion
Chilled Beams + DC Alternate
[GOAL]
To reduce energy consumption and carbon footprint compared to the original system.
INTRODUCTION
DEPTH I
DEPTH II
DEPTH III
GOAL
OPERATION
RESULTS
COST & SAVINGS
EMISSIONS
BREADTH I
CONCLUSION
ACKNOWLEDGEMENTS
QUESTIONS
75 Ames Street:
Nathaniel Mooney

## Slide 24
The Broad Institute Expansion
INTRODUCTION
DEPTH I
DEPTH II
DEPTH III
GOAL
OPERATION
RESULTS
COST & SAVINGS
EMISSIONS
BREADTH I
CONCLUSION
ACKNOWLEDGEMENTS
QUESTIONS
[OPERATION]
Combine The Aircuity-Optinet system in labs with a chilled beam system using the design criteria from depth I & II already mentioned
Chilled Beams + DC Alternate
75 Ames Street:
Nathaniel Mooney

## Slide 25
The Broad Institute Expansion
[RESULTS]
INTRODUCTION
DEPTH I
DEPTH II
DEPTH III
GOAL
OPERATION
RESULTS
COST & SAVINGS
EMISSIONS
BREADTH I
CONCLUSION
ACKNOWLEDGEMENTS
QUESTIONS
 | Electricity (kWh) | Natural Gas (Therms) | Electricity Cost Per year | Natural Gas Cost per year | Total Cost Per Year
Original System | 9,985,524.00 | 107,047.00 | $2,007,090.32 | $170,954.06 | $2,178,044.38
Chilled Beams + DCV | 7,493,006.00 | 42,136.00 | $1,506,094.21 | $67,291.19 | $1,573,385.40
Difference | 2,492,518.00 | 64,911.00 | $500,996.12 | $103,662.87 | $604,658.99
 |  |  |  | % change | -28%
Chart: 75 Ames Electricity Use Comparisons [10^6 BTU/YR]
| Original System VAV Reheat | Alternate Chilled Beams | Alternate DCV | Alternate DCV + Chilled Beams
Lighting | 3827.3 | 3823.3 | 3827.3 | 3827.3
Space Heating | 408.8 | 503.8 | 511.6 | 410.7
Space Cooling | 2551.1 | 2467.6 | 2553.5 | 2370.9
Pumps | 789.6 | 708.2 | 825.9 | 629.7
Heat Rejection | 1412.4 | 1648.2 | 1415.8 | 1665.3
Fans | 13973.8 | 6418.8 | 10608.6 | 6432.8
Recepticles | 11117.6 | 11110.9 | 11177.5 | 10237
Chart: Chilled Beams + DCV Monthly Electrical Use Vs. Original VAV System
| Jan | Feb | Mar | Apr | May | June | July | Aug | Sept | Oct | Nov | Dec
Alternate DCV + Chilled Beams Electric KWH | 548035 | 495704 | 605777 | 560347 | 671149 | 723652 | 714222 | 766212 | 639455 | 667724 | 581212 | 519517
Original System VAV Reheat | 721666 | 654882 | 791432 | 746783 | 894909 | 978922 | 962894 | 1040655 | 847768 | 895855 | 771446 | 678311
Chart: Chilled Beams and DCV
| Lighting | Space Heating | Space Cooling | Pumps | Heat Rejection | Fans | Recepticles
 | 3827.3 | 410.7 | 2370.9 | 629.7 | 1665.3 | 6432.8 | 10237
Chart: 
| Jan | Feb | Mar | Apr | May | June | July | Aug | Sept | Oct | Nov | Dec
Alternate DCV + Chilled Beams Gas Therms | 7914 | 7560 | 4379 | 2278 | 1631 | 1095 | 369 | 947 | 1604 | 1935 | 3083 | 9343
Original System VAV Reheat Gas Therms | 17302 | 16453 | 10610 | 6680 | 6230 | 4318 | 1243 | 3556 | 6004 | 7054 | 8173 | 19423
Chilled Beams + DC Alternate
75 Ames Street:
Nathaniel Mooney

## Slide 26
The Broad Institute Expansion
[RESULTS]
INTRODUCTION
DEPTH I
DEPTH II
DEPTH III
GOAL
OPERATION
RESULTS
COST & SAVINGS
EMISSIONS
BREADTH I
CONCLUSION
ACKNOWLEDGEMENTS
QUESTIONS
 | Electricity (kWh) | Natural Gas (Therms) | Electricity Cost Per year | Natural Gas Cost per year | Total Cost Per Year
Original System | 9,985,524.00 | 107,047.00 | $2,007,090.32 | $170,954.06 | $2,178,044.38
Chilled Beams + DCV | 7,493,006.00 | 42,136.00 | $1,506,094.21 | $67,291.19 | $1,573,385.40
Difference | 2,492,518.00 | 64,911.00 | $500,996.12 | $103,662.87 | $604,658.99
 |  |  |  | % change | -28%
Chart: 75 Ames Electricity Use Comparisons [10^6 BTU/YR]
| Original System VAV Reheat | Alternate Chilled Beams | Alternate DCV | Alternate DCV + Chilled Beams
Lighting | 3827.3 | 3823.3 | 3827.3 | 3827.3
Space Heating | 408.8 | 503.8 | 511.6 | 410.7
Space Cooling | 2551.1 | 2467.6 | 2553.5 | 2370.9
Pumps | 789.6 | 708.2 | 825.9 | 629.7
Heat Rejection | 1412.4 | 1648.2 | 1415.8 | 1665.3
Fans | 13973.8 | 6418.8 | 10608.6 | 6432.8
Recepticles | 11117.6 | 11110.9 | 11177.5 | 10237
Chart: 
| Jan | Feb | Mar | Apr | May | June | July | Aug | Sept | Oct | Nov | Dec
Alternate DCV + Chilled Beams Electric KWH | 548035 | 495704 | 605777 | 560347 | 671149 | 723652 | 714222 | 766212 | 639455 | 667724 | 581212 | 519517
Original System VAV Reheat | 721666 | 654882 | 791432 | 746783 | 894909 | 978922 | 962894 | 1040655 | 847768 | 895855 | 771446 | 678311
Chart: Chilled Beams and DCV
| Lighting | Space Heating | Space Cooling | Pumps | Heat Rejection | Fans | Recepticles
 | 3827.3 | 410.7 | 2370.9 | 629.7 | 1665.3 | 6432.8 | 10237
Chart: 
| Jan | Feb | Mar | Apr | May | June | July | Aug | Sept | Oct | Nov | Dec
Alternate DCV + Chilled Beams Gas Therms | 7914 | 7560 | 4379 | 2278 | 1631 | 1095 | 369 | 947 | 1604 | 1935 | 3083 | 9343
Original System VAV Reheat Gas Therms | 17302 | 16453 | 10610 | 6680 | 6230 | 4318 | 1243 | 3556 | 6004 | 7054 | 8173 | 19423
Chilled Beams + DC Alternate
75 Ames Street:
Nathaniel Mooney

## Slide 27
The Broad Institute Expansion
[RESULTS]
INTRODUCTION
DEPTH I
DEPTH II
DEPTH III
GOAL
OPERATION
RESULTS
COST & SAVINGS
EMISSIONS
BREADTH I
CONCLUSION
ACKNOWLEDGEMENTS
QUESTIONS
 | Electricity (kWh) | Natural Gas (Therms) | Electricity Cost Per year | Natural Gas Cost per year | Total Cost Per Year
Original System | 9,985,524.00 | 107,047.00 | $2,007,090.32 | $170,954.06 | $2,178,044.38
Chilled Beams + DCV | 7,493,006.00 | 42,136.00 | $1,506,094.21 | $67,291.19 | $1,573,385.40
Difference | 2,492,518.00 | 64,911.00 | $500,996.12 | $103,662.87 | $604,658.99
 |  |  |  | % change | -28%
Chart: 75 Ames Electricity Use Comparisons [10^6 BTU/YR]
| Original System VAV Reheat | Alternate Chilled Beams | Alternate DCV | Alternate DCV + Chilled Beams
Lighting | 3827.3 | 3823.3 | 3827.3 | 3827.3
Space Heating | 408.8 | 503.8 | 511.6 | 410.7
Space Cooling | 2551.1 | 2467.6 | 2553.5 | 2370.9
Pumps | 789.6 | 708.2 | 825.9 | 629.7
Heat Rejection | 1412.4 | 1648.2 | 1415.8 | 1665.3
Fans | 13973.8 | 6418.8 | 10608.6 | 6432.8
Recepticles | 11117.6 | 11110.9 | 11177.5 | 10237
Chart: 
| Jan | Feb | Mar | Apr | May | June | July | Aug | Sept | Oct | Nov | Dec
Alternate DCV + Chilled Beams Electric KWH | 548035 | 495704 | 605777 | 560347 | 671149 | 723652 | 714222 | 766212 | 639455 | 667724 | 581212 | 519517
Original System VAV Reheat | 721666 | 654882 | 791432 | 746783 | 894909 | 978922 | 962894 | 1040655 | 847768 | 895855 | 771446 | 678311
Chart: Chilled Beams and DCV
| Lighting | Space Heating | Space Cooling | Pumps | Heat Rejection | Fans | Recepticles
 | 3827.3 | 410.7 | 2370.9 | 629.7 | 1665.3 | 6432.8 | 10237
Chart: Chilled Beams + DCV Vs. Original System Heating
| Jan | Feb | Mar | Apr | May | June | July | Aug | Sept | Oct | Nov | Dec
Alternate DCV + Chilled Beams Gas Therms | 7914 | 7560 | 4379 | 2278 | 1631 | 1095 | 369 | 947 | 1604 | 1935 | 3083 | 9343
Original System VAV Reheat Gas Therms | 17302 | 16453 | 10610 | 6680 | 6230 | 4318 | 1243 | 3556 | 6004 | 7054 | 8173 | 19423
Chilled Beams + DC Alternate
75 Ames Street:
Nathaniel Mooney

## Slide 28
The Broad Institute Expansion
INTRODUCTION
DEPTH I
DEPTH II
DEPTH III
GOAL
OPERATION
RESULTS
COST & SAVINGS
EMISSIONS
BREADTH I
CONCLUSION
ACKNOWLEDGEMENTS
QUESTIONS
With 2.5% inflation |  |  |  |  | 
10 Year Life Cycle Cost Analysis |  |  |  |  | 
YEAR | Original System VAV Reheat | DCV + Chilled Beams Alternate | Savings | With Maintenance First Year Free | Savings
0 | $- | $903,167.79 | $(903,167.79) | $903,167.79 | $(903,167.79)
1 | $2,123,593.27 | $2,414,639.36 | $(291,046.08) | $2,414,639.36 | $(291,046.08)
2 | $4,141,006.88 | $3,849,972.87 | $291,034.01 | $3,869,900.82 | $271,106.06
3 | $6,056,222.57 | $5,212,030.55 | $844,192.01 | $5,250,890.06 | $805,332.51
4 | $7,873,089.34 | $6,503,579.12 | $1,369,510.22 | $6,560,411.15 | $1,312,678.19
5 | $9,595,327.63 | $7,727,292.74 | $1,868,034.89 | $7,801,174.38 | $1,794,153.25
6 | $11,226,533.33 | $8,885,755.94 | $2,340,777.38 | $8,975,799.19 | $2,250,734.14
7 | $12,770,181.66 | $9,981,466.43 | $2,788,715.23 | $10,086,817.02 | $2,683,364.64
8 | $14,229,630.99 | $11,016,837.79 | $3,212,793.20 | $11,136,674.09 | $3,092,956.90
9 | $15,608,126.49 | $11,994,202.17 | $3,613,924.33 | $12,127,734.05 | $3,480,392.45
10 | $16,908,803.70 | $12,915,812.80 | $3,992,990.90 | $13,062,280.58 | $3,846,523.12
[COST & SAVINGS]
First Cost
Chilled Beams + Aircuity = $903,167.79
Annual Savings
$604,658.99
Pay back
1.5 years
Chilled Beams + DC Alternate
75 Ames Street:
Nathaniel Mooney

## Slide 29
The Broad Institute Expansion
[EMISSIONS]
INTRODUCTION
DEPTH I
DEPTH II
DEPTH III
GOAL
OPERATION
RESULTS
COST & SAVINGS
EMISSIONS
BREADTH I
CONCLUSION
ACKNOWLEDGEMENTS
QUESTIONS
ENVIRONMENTAL IMPACT |  |  |  |  | 
Pollutant | Unit | Original System VAV Reheat | DCV & Chilled Beams Alternate | % Change | Difference
CO2 | lbm/yr | 876,396,480 | 657,636,416 | -24.96% | 218,760,064
SO2 | gm/yr | 2,742,078 | 2,057,619 | -24.96% | 684,459
NOX | gm/yr | 742,165 | 556,911 | -24.96% | 185,254
Chilled Beams + DC Alternate
75 Ames Street:
Nathaniel Mooney

## Slide 30
The Broad Institute Expansion
[GOAL]
To size the new electrical equipment (wires, conduit, breakers, starters) serving the new fans and chilled water pump for the chilled beam system
INTRODUCTION
DEPTH I
DEPTH II
DEPTH III
BREADTH I
GOAL
  METHOD
RESULT
CONCLUSION
ACKNOWLEDGEMENTS
QUESTIONS
Electrical Breadth
75 Ames Street:
Nathaniel Mooney

## Slide 31
The Broad Institute Expansion
[Method]
Fan HP found using fan affinity laws
FLC
      Table 430.250 Full load Current Three-Phase Alternating Current from NEC 2011
Find KVA
      FLA=KVA / (Voltage√(3)) KVA = (Voltage)(√(3))(FLA)
Wire Size
      1.25 for continuous loads
      Table 310.15(B)(16) from NEC 2-11
      THWN Type wire Copper
      Rated 75C
Electrical Breadth
Circuit Breaker
    2.5 multiplier
    Table 430.52 NEC 2011
    Next lowest breaker chosen
Ground Wire
    Based on breaker size
    Table 250.122 NEC 2011
Conduit
    Table C.1 NEC 2011
    EMT
INTRODUCTION
DEPTH I
DEPTH II
DEPTH III
BREADTH I
GOAL
  METHOD
RESULT
CONCLUSION
ACKNOWLEDGEMENTS
QUESTIONS
75 Ames Street:
Nathaniel Mooney

## Slide 32
The Broad Institute Expansion
[Method]
Starter
Disconnect
Electrical Breadth
Redesign |  |  |  |  |  | 
UNIT | UNIT # | Volt | Phase | Fan HP | FLA | kVA
AHU1 | SF1 | 480 | 3 | 52.82 | 65 | 54
 | SF2 | 480 | 3 | 52.82 | 65 | 54
 | SF3 | 480 | 3 | 52.82 | 65 | 54
 | SF4 | 480 | 3 | 52.82 | 65 | 54
EAHU1 | EF1 | 480 | 3 | 29.75 | 34 | 28
 | EF2 | 480 | 3 | 29.75 | 34 | 28
 | EF3 | 480 | 3 | 29.75 | 34 | 28
 | EF4 | 480 | 3 | 29.75 | 34 | 28
 | EF5 | 480 | 3 | 29.75 | 34 | 28
CHWP | CHILLED BEAMS | 480 | 3 | 35 | 40 | 33
Disconnect
    Standard Sizes 30, 60, 100, and 200 amps
    Next higher disconnect is chosen based on the FLC.
INTRODUCTION
DEPTH I
DEPTH II
DEPTH III
BREADTH I
GOAL
  METHOD
RESULT
CONCLUSION
ACKNOWLEDGEMENTS
QUESTIONS
75 Ames Street:
Nathaniel Mooney

## Slide 33
The Broad Institute Expansion
[RESULT]
Electrical Breadth
INTRODUCTION
DEPTH I
DEPTH II
DEPTH III
BREADTH I
GOAL
  METHOD
RESULT
CONCLUSION
ACKNOWLEDGEMENTS
QUESTIONS
75 Ames Street:
Nathaniel Mooney

## Slide 34
The Broad Institute Expansion
Chilled Beams Alternate
[CONCLUSION]
    Chilled Beams coupled with Aircutiy demand controlled ventilation offers the best energy savings ($604,658.99) and environmental savings.
    Reduction of Air Handlers off sets most of the costs
    $20,963 maintenance important for keeping system working properly
    reasonable Payback 1.5 years
INTRODUCTION
DEPTH I
DEPTH II
DEPTH III
BREADTH I
CONCLUSION
ACKNOWLEDGEMENTS
QUESTIONS
75 Ames Street:
Nathaniel Mooney

## Slide 35
`
The Broad Institute Expansion
THANK YOU TO…
INTRODUCTION
DEPTH I
DEPTH II
DEPTH III
BREADTH I
CONCLUSION
ACKNOWLEDGEMENTS
QUESTIONS
BR+A
The Broad Institute
ElLKUS|MANFRDI Architects
Entire Project Design and Construction Team
Bryan Donovan
Tom Kolsun
Dr. William Bahnfleth
M. Kevin Parfitt, P.E.
Bob Holland
Corey Wilkinson
Friends and Family
AE Class 2013
75 Ames Street:
Nathaniel Mooney

## Slide 36
The Broad Institute Expansion
INTRODUCTION
DEPTH I
DEPTH II
DEPTH III
BREADTH I
CONCLUSION
ACKNOWLEDGEMENTS
QUESTIONS
And Thank You For Your Time…
75 Ames Street:
Nathaniel Mooney

## Slide 37
The Broad Institute Expansion
Aircuity Rooms:
Chosen Based On:
  Size
  ACH
    Labs 6/12
    Tissue Culture 6/15
INTRODUCTION
DEPTH I
DEPTH II
DEPTH III
BREADTH I
CONCLUSION
ACKNOWLEDGEMENTS
QUESTIONS
75 Ames Street:
Nathaniel Mooney

## Slide 38
The Broad Institute Expansion
Typical Building Loads
INTRODUCTION
DEPTH I
DEPTH II
DEPTH III
BREADTH I
CONCLUSION
ACKNOWLEDGEMENTS
QUESTIONS
Questions…
75 Ames Street:
Nathaniel Mooney

## Slide 39
The Broad Institute Expansion
Pump Size
Q=500 x GPM x DT
DT=5
Q= 4582210 BTU/HR
GPM=1832.884
INTRODUCTION
DEPTH I
DEPTH II
DEPTH III
BREADTH I
CONCLUSION
ACKNOWLEDGEMENTS
QUESTIONS
75 Ames Street:
Nathaniel Mooney

## Slide 40
The Broad Institute Expansion
Chilled Beam Control
  On VAV
  Vary water flow rate through beam using zone level thermostats
    7-8 degree change can change cooling rates of beams by 60%
  Dew point sensors can be used in spaces where concern of condensation is high
    Resets water temperature higher to prevent condensation
  Beam supply varied by 2 way on-off control valve controlled by zone thermostat.
INTRODUCTION
DEPTH I
DEPTH II
DEPTH III
BREADTH I
CONCLUSION
ACKNOWLEDGEMENTS
QUESTIONS
75 Ames Street:
Nathaniel Mooney