## Slide 1
ELEMENTARY SCHOOL ONE
TOWN, MARYLAND
Jonathan Cann
Mechanical Option Advisor: Dr. Treado
BAE/MAE Integrated Program Spring 2015
www.janneyschool.org
www.nps.gov/nr/

## Slide 2
Mechanical Option
Elementary School One
Jonathan Cann
N
Project Background
Existing Conditions
Proposal
Mechanical Depth
Acoustical Breadth
Conclusion
Building Statistics
Existing Building: Built 1925
National Register of Historic Places
Gross Square Feet : 84,400
Overall Project Budget: $25 Million
Completion Date: August 2011
3 stories above grade, 1 below
Function: Educational
Presentation Outline
maps.google.com

## Slide 3
Mechanical Option
Elementary School One
Jonathan Cann
N
Project Background
Existing Conditions
Proposal
Mechanical Depth
Acoustical Breadth
Conclusion
Location and Weather
 | Summer | Winter
Designed Dry Bulb (°F) | 91 | 13
Designed Wet Bulb (°F) | 77 | -
Indoor Air Temperature (°F) | 75 | 72
Weather data based on Baltimore, Maryland
Town, Maryland
Relative Humidity – 50%
Presentation Outline
www.ashrae.org

## Slide 4
Mechanical Option
Elementary School One
Jonathan Cann
N
Project Background
Existing Conditions
Proposal
Mechanical Depth
Acoustical Breadth
Conclusion
Basement
Second Floor
Third Floor
First Floor
Mechanical Layout
Blue: RTU-1 & 2 Cafeteria
Orange: RTU-3 &4 (DOAS) and VRF
Purple: RTU- 5 (DOAS) and VRF
Green: RTU-6 & 7 Multipurpose
Red: AHU-1 Administrative Offices
Presentation Outline

## Slide 5
Mechanical Option
Elementary School One
Jonathan Cann
N
Project Background
Existing Conditions
Proposal
Mechanical Depth
Acoustical Breadth
Conclusion
Rooftop Unit Schedule |  |  | 
Unit No. | Area Served | Supply CFM | Total Load (MBH)
RTU-1 | Cafeteria | 7500 | 227
RTU-2 | Cafeteria | 7500 | 227
RTU-3 | Exist. Bldg. | 8300 | 350
RTU-4 | Exist. Bldg. | 5600 | 236.9
RTU-5 | Addition | 10650 | 538
RTU-6 | Multi-purpose | 7500 | 235
RTU-7 | Multi-purpose | 7500 | 235
Air Cooled Condensing Units Schedules (VRF System) |  |  | 
Unit No. | Cooling (MBH) | Heating (MBH) | Condenser CFM
CU-VRF-1 | 439 | 494 | 20100
CU-VRF-2 | 343 | 386 | 20100
CU-VRF-3 | 305 | 343 | 13400
Mechanical Schedule
Presentation Outline
www.daikin.com

## Slide 6
Mechanical Option
Elementary School One
Jonathan Cann
N
Project Background
Existing Conditions
Proposal
Mechanical Depth
Acoustical Breadth
Conclusion
RTU- 1, 2, 6 & 7
RTU- 3, 4, & 5
DOAS
VRF System
Mechanical Schematics
Presentation Outline

## Slide 7
Mechanical Option
Elementary School One
Jonathan Cann
N
Project Background
Existing Conditions
Proposal
Mechanical Depth
Acoustical Breadth
Conclusion
 | % of Total Building Energy | Total Building Energy (kBtu/yr)
Heating | 21.56% | 894,258
Cooling | 30.80% | 1,277,511
Receptacles | 0.51% | 21,069
Lighting | 47.13% | 1,954,985
Total | 100% | 4,147,823
 | CO2 (lbm/year) | SO2 (gm/year) | NOx (gm/year)
Building Emissions | 1,626,597.0 | 14,638.5 | 2,801.8
Energy Use & Emissions
Presentation Outline

## Slide 8
Mechanical Option
Elementary School One
Jonathan Cann
N
Project Background
Existing Conditions
Proposal
Mechanical Depth
Acoustical Breadth
Conclusion
Proposal Goals
Depth: Implement a geothermal system to improve the buildings energy use.
Breadth: The impact of a geothermal system on the construction management of the project.
Breadth: Perform acoustical analysis to insure the comfort of the spaces
Presentation Outline
www.nps.gov/nr/

## Slide 9
Mechanical Option
Elementary School One
Jonathan Cann
N
Project Background
Existing Conditions
Proposal
Mechanical Depth
Acoustical Breadth
Conclusion
Proposed System
Water-cooled VRF units coupled with closed loop ground coupled heat pump
More efficient than air-cooled condensers
Constant thermal properties
Reduces noise pollution
Minimal site area loss
High initial cost (long term owners)
Renewable energy source (earth)
Low maintenance
Presentation Outline
Ball State University

## Slide 10
Mechanical Option
Elementary School One
Jonathan Cann
N
Project Background
Existing Conditions
Proposal
Mechanical Depth
Acoustical Breadth
Conclusion
Soil Properties | Wet dense sand
Dry Density | 120 lb/ft^3
Conductivity (k) | 1.63 Btu/h*ft*°F
Diffusivity (α) | 0.91 ft^2/day
Well Design Details |  | 
Radius of bore | 0.42 | ft
SDR 11 | 1.00 | in
Rpipe | 0.10 | ft*hr*°F/Btu
Rgrout | 0.05 | ft*hr*°F/Btu
Rbore | 0.15 | ft*hr*°F/Btu
Site & Well Properties
Annual Average Ground Temperature - 55ºF
Presentation Outline
Geothermal Heat Pump Design Manual by McQuay Air Conditioning

## Slide 11
Mechanical Option
Elementary School One
Jonathan Cann
N
Project Background
Existing Conditions
Proposal
Mechanical Depth
Acoustical Breadth
Conclusion
 | Symbol | Cooling | Heating | Units
Net annual average heat transfer to the ground | Qa | 251,250 | 150,000 | Btu/h
Building design cooling block load (or heating) | Qlc (or Qlh) | 2,010,000 | 1,200,000 | Btu/h
Power input at design cooling load (or heating) | Wc (or Wh) | 130,000 | 130,000 | W
Effective thermal resistance of ground annual pulse | Rga | 0.2438 | 0.2438 | ft*hr*°F/Btu
Effective thermal resistance of ground monthly pulse | Rgm | 0.223 | 0.223 | ft*hr*°F/Btu
Effective thermal resistance of ground daily pulse | Rgd | 0.131 | 0.131 | ft*hr*°F/Btu
Thermal resistance of bore | Rb | 0.15 | 0.15 | ft*hr*°F/Btu
Short circuit heat loss factor | Fsc | 1.04 | 1.04 | 
Part load factor during design month | PLFm | 1.00 | 1.00 | 
Undisturbed ground temperature | tg | 55 | 55 | °F
Liquid temperature at heat pump inlet | twi | 74 | 44 | °F
Liquid temperature at heat pump outlet | two | 83 | 36 | °F
Temperature penalty | tp | 2.00 | 2.00 | °F
 | Length | 33,689 | 32,454 | ft
 | # of wells | 84.2 | 81.1 | 
Geothermal Calculations
Required Bore Length for Cooling (ft)
Required Bore Length for Heating (ft)
Equations from ASHRAE Handbook
Presentation Outline

## Slide 12
Mechanical Option
Elementary School One
Jonathan Cann
N
Project Background
Existing Conditions
Proposal
Mechanical Depth
Acoustical Breadth
Conclusion
85 wells
400 ft deep wells
15 ft well spacing
Area used 19,125 sq. ft.
Pump located in East Mechanical Room
Direct return piping
Well Layout
1
2,3
Presentation Outline
maps.google.com

## Slide 13
Mechanical Option
Elementary School One
Jonathan Cann
N
480 GPM
2.9 GPM/ton design
6” header pipe
2” row pipe
1” well U-tube
5” bore diameter
Pipe & Flow Design
Project Background
Existing Conditions
Proposal
Mechanical Depth
Acoustical Breadth
Conclusion
Presentation Outline
www.kochergeowelldrilling.com

## Slide 14
Mechanical Option
Elementary School One
Jonathan Cann
N
Table 22- Head Loss | 
Friction Loss | 6.8 ft
Fixture Loss | 109 ft
Velocity Loss | 0.4 ft
Total head loss | 116.2 ft
Size | Head | Flow Rate | RPM | HP | Manufacturer | Model
4x4x7 | 116.2 ft | 480 gpm | 3500 | 20 | Goulds | AC-135.3F
Well Pump Selection
Project Background
Existing Conditions
Proposal
Mechanical Depth
Acoustical Breadth
Conclusion
Presentation Outline
www.goulds.com
www.goulds.com

## Slide 15
Mechanical Option
Elementary School One
Jonathan Cann
N
 | Daikin | VRV-WIII Series |  |  |  | 
 | Unit | 21 ton | 18 ton | 12 ton | 7 ton | 6 ton
Cooling | Capacity (Btu/h) | 252,000 | 216,000 | 144,000 | 84,000 | 72,000
 | EER | 15.0 | 15.3 | 15.3 | 15.0 | 15.3
Heating | Capacity (Btu/h) | 283,500 | 243,000 | 162,000 | 94,000 | 81,000
 | COP | 4.7 | 5.3 | 5.3 | 4.7 | 5.3
 | Units
CU-VRF-1 | (3)x 21 ton + 12 ton
CU-VRF-2 | (2)x 21 ton + 7 ton
CU-VRF-3 | 21 ton + 18 ton + 6 ton
Water-Cooled VRF Unit Selection
Unified heat pump and heat recovery
Units in series to reach needed capacity
Self heat recovery between modules
Project Background
Existing Conditions
Proposal
Mechanical Depth
Acoustical Breadth
Conclusion
Presentation Outline
www.daikin.com

## Slide 16
Mechanical Option
Elementary School One
Jonathan Cann
N
 | Water |  |  | Refrigerant |  |  | Indoor Units Air | 
 | Tin | Tout | GPM | Tin | Tout | GPM | Supply | Return
Cooling | 74°F | 83°F | 480 | 76°F | 50°F | 280 | 53-55°F | 78-80°F
Heating | 44°F | 36°F | 480 | 105°F | 89°F | 280 | 78-81°F | 68-70°F
Heat Exchanger Details
Ground Temperature 55ºF
Ground Coupled Side
20% glycol / 80% water
VRF Side
R140a
Refrigerant | Q (tons) | Refrigerant Impact per ton | Credit (<100)
R-410a | 324 | 95.7 | Yes
EA Credit 6
Project Background
Existing Conditions
Proposal
Mechanical Depth
Acoustical Breadth
Conclusion
Presentation Outline
www.dreamstime.com

## Slide 17
Mechanical Option
Elementary School One
Jonathan Cann
N
Table 25- Alternative Yearly Energy Consumption |  |  | 
 | Building | Building | Source
 | kWh | kBtu/yr | kBtu/yr
Heating | 185,431 | 632,320 | 1,896,960
Cooling | 192,269 | 656,215 | 1,968,843
Lighting | 572,805 | 1,954,985 | 5,865,541
Receptacle | 6,173 | 21,069 | 63,213
Total | 956,678 | 3,264,589 | 9,794,557
Cost | $131,064.90 |  | 
Alternative System Energy Use
Project Background
Existing Conditions
Proposal
Mechanical Depth
Acoustical Breadth
Conclusion
Presentation Outline

## Slide 18
Mechanical Option
Elementary School One
Jonathan Cann
N
Table 26- Yearly Energy Breakdown |  |  |  | 
 | Building (kWh) | Building (kBtu/yr) | Source (kBtu/yr) | Cost
Original System | 1,215,300 | 4,147,823 | 12,444,711 | $166,496.09
Alternative System | 956,678 | 3,264,589 | 9,794,557 | $131,064.90
Yearly Savings | 258,622 | 883,234 | 2,650,154 | $35,431.19
 | CO2 (lbm/year) | SO2 (gm/year) | NOx (gm/year)
Original Design | 1,626,597.0 | 14,638.5 | 2,801.8
Alternative Design | 1,280,231.0 | 11,521.4 | 2,205.2
Energy & Emissions Comparison
Emissions Comparison- 21.3% less
Project Background
Existing Conditions
Proposal
Mechanical Depth
Acoustical Breadth
Conclusion
Presentation Outline

## Slide 19
Mechanical Option
Elementary School One
Jonathan Cann
N
Table 28- Payback Period |  | 
 | Cost | 
Original System | $56,348.44 | 
Alternative System | $692,071.26 | 
With 10% Rebate | $622,564.13 | 
System Difference | $566,215.69 | 
Yearly Energy Savings | $35,431.19 | 
Payback Period | 15.98 | Years
 | 191.77 | Months
Federal Tax Rebate
10 % of initial material and labor cost
EER ≥ 14.1
COP ≥ 3.3
Without rebate Payback Period = 19.53 years
Payback Period
Project Background
Existing Conditions
Proposal
Mechanical Depth
Acoustical Breadth
Conclusion
Presentation Outline

## Slide 20
Mechanical Option
Elementary School One
Jonathan Cann
N
Original Building cost is based on 2015 using inflation from 2010.
Original |  | 
Material | Condensers | $42,377.00
 | Controls | $823.00
Labor | Condensers | $11,985.00
 | Controls | $1,163.00
Total Cost |  | $56,348.00
Alternative |  | 
Material | Pump | $19,200
 | Antifreeze | $6,786
 | Water | $14
 | Controls | $1,475
 | Investigation | $915
 | Loop | $424,521
 | Sub-total | $452,911
Labor | Pump | $1,842
 | Controls | $2,952
 | Investigation | $3,993
 | Loop | $230,373
 | Sub-total | $239,160
Total Cost |  | $692,071
 | Mechanical Cost | Total Construction Cost
Original Design | $3,461,864 | $20,969,617
Alternative Design | $4,028,079 | $21,535,833
Percent Increase | 16.4% | 2.7%
Cost Comparison
Project Background
Existing Conditions
Proposal
Mechanical Depth
Acoustical Breadth
Conclusion
Presentation Outline
maps.google.com

## Slide 21
Mechanical Option
Elementary School One
Jonathan Cann
Project Background
Existing Conditions
Proposal
Mechanical Depth
Acoustical Breadth
Conclusion
Multi-purpose Room Acoustical Treatment
Before: NC > 65 After: NC – 39
Added Treatment:
2” duct lining (60 ft each)
One duct silencer each
Cost Breakdown
Duct lining = $11,457
Duct Silencers= $4,700
Total Cost = $16,157
Goal NC-45
Presentation Outline

## Slide 22
Mechanical Option
Elementary School One
Jonathan Cann
Cafeteria Acoustical Treatment
Before: NC - 52 After: NC – 41
Added Treatment:
One duct silencer each (36”x12”x50”)
Cost Breakdown
Duct Silencers= $4,000
Total Cost = $4,000
Not recommended extra cost
Goal NC-45
Project Background
Existing Conditions
Proposal
Mechanical Depth
Acoustical Breadth
Conclusion
Presentation Outline

## Slide 23
Mechanical Option
Elementary School One
Jonathan Cann
Project Background
Existing Conditions
Proposal
Mechanical Depth
Acoustical Breadth
Conclusion
Conclusion
System Initial Cost - $692,071.26
Monthly Savings - $2952.60
Payback Period of System – 15.98 years
EUI Reduction – 21.3%
Presentation Outline
ww.nbm.org
www.nps.gov/nr/

## Slide 24
Mechanical Option
Elementary School One
Jonathan Cann
Acknowledgements
Penn State Faculty
JVP Engineers
Dr. Stephen Treado
All my peers that helped during the process
All my friends and family for their support
www.kumicm.com
www.nps.gov/nr/

## Slide 25
Mechanical Option
Elementary School One
Jonathan Cann
Questions?
www.kumicm.com
www.nps.gov/nr/