## Slide 1
Carl R. Darnall Army Medical Center
Marissa Caldwell
Mechanical Option

## Slide 2
Building overview
Thesis Goals
Depth
Dedicated Outdoor Air System
Variable Refrigerant Flow
Water Source Heat Pump
Air Quality Analysis
Energy Comparison
Structural Breadth
Construction Breadth
Conclusion
Carl R. Darnall Army Medical Center

## Slide 3
Building Overview
Building overview
Thesis Goals
Depth
Dedicated Outdoor Air System
Variable Refrigerant Flow
Water Source Heat Pump
Air Quality Analysis
Energy Comparison
Structural Breadth
Construction Breadth
Conclusion
Owner: Army Corps of Engineers
Department of Defense – UFC Standard 4-510
Located on Fort Hood Base, outside of Killeen, TX
Floor Area: 900,000 sq ft
Replacing the current Carl R. Darnall Army Medical Center across street
Notes: Army Corps of Engineers is the owner of the building, so strict design criteria was used by implementing UFC 4-510 which is the unified facilities criteria whole building design guide. In between each floor of medical spaces and offices are interstitial floors. These interstitial floors, like the rendering on the right, house the communication, medical gas, Pneumatic tube, electrical and mechanical systems. Designed strictly for a facilities maintenance employee and a cart, the IBS floors are designed for low dead and live loads. Since the CAVs are located in this space, monthly maintenance is easy to do.

## Slide 4
Building Overview
Level 5
Level 6
Building overview
Thesis Goals
Depth
Dedicated Outdoor Air System
Variable Refrigerant Flow
Water Source Heat Pump
Air Quality Analysis
Energy Comparison
Structural Breadth
Construction Breadth
Conclusion
Patient Rooms
Medical Support
Offices
Conference
Library
Notes: Since this building is massive, the top two floors of the bed tower were analyzed for
Red are patient rooms, purple is medical support space
Green are offices, purple are conference rooms, red/orange is a library

## Slide 5
Building Overview
Level 5
Level 6
Building overview
Thesis Goals
Depth
Dedicated Outdoor Air System
Variable Refrigerant Flow
Water Source Heat Pump
Air Quality Analysis
Energy Comparison
Structural Breadth
Construction Breadth
Conclusion
Notes: Since this building is massive, the top two floors of the bed tower were analyzed for
Red are patient rooms, purple is medical support space
Green are offices, purple are conference rooms, red/orange is a library

## Slide 6
Mechanical System
Cooling System
Heating System
(4) 11,700 MBH steam boilers
Low Nox burner & boiler stack economizer
(3) Steam to water heat exchanger
Steam for humidification & sterile equipment
Provides 140°F to AHUs and CAVs
(4) 1,300 ton centrifugal chillers
(4) 18,000 MBH cooling towers
200 ton heat recovery chiller
  Domestic hot water & chilled water
Provides 44°F to AHUs
Building overview
Thesis Goals
Depth
Dedicated Outdoor Air System
Variable Refrigerant Flow
Water Source Heat Pump
Air Quality Analysis
Energy Comparison
Structural Breadth
Construction Breadth
Conclusion
Notes: As previously mentioned, the central utility plant is located off site, just feet from the hospital. All services provided are transported via the utility tunnel connecting the CUP to the main building. The mechanical system comprises of a steam system and a chilled water system. The Cooling system comprises of 4 1,300 centrifugal chillers, 4 18,000 MBH cooling towers and 1 200 ton heat recovery chiller. The heat recovery chiller provides pre heating for the domestic hot water and provides a chilled water base load. For the heating system, there are four 11700 MBH steam boilers and 3 steam to water shell and tube heat exchangers provides 140F hot water to CAVs and AHUs. Steam boiler along with the boiler stack economizer allow for the 85% efficiency. Steam is provided for humidification & sterile equipment, as well as kitchen equipment.

## Slide 7
Mechanical System
Airside System
Enthalpy wheel to precondition outdoor air
(2) 45,000 cfm air handler providing 55°F air
Constant Air Volume terminal units with reheat
HWS 140°F
CHWS 44°F
SHU
ENTHALPY
SUPPLY AIR
HEATING COIL
HUMIDIFIER
COOLING COIL
FAN
FILTER
HWR 110°F
CHWR 60°F
SHUC
PRE-CONDITIONED OUTDOOR
AIR
Building overview
Thesis Goals
Depth
Dedicated Outdoor Air System
Variable Refrigerant Flow
Water Source Heat Pump
Air Quality Analysis
Energy Comparison
Structural Breadth
Construction Breadth
Conclusion
General Exhaust
WHEEL
General Exhaust
Notes: Each floor is provided conditioned 55F outdoor air by a dedicated outdoor air system in the penthouse. The dedicated outdoor air handlers provide preconditioned air at 55F to the constant air volume terminal units located in the interstitial space. The CAVs are arranged one per patient room and they supply 100% outdoor air to condition the space.

## Slide 8
Reduce Energy
Safe Community
Economically Feasible
Structurally Stable
Building overview
Thesis Goals
Depth
Dedicated Outdoor Air System
Variable Refrigerant Flow
Water Source Heat Pump
Air Quality Analysis
Energy Comparison
Structural Breadth
Construction Breadth
Conclusion

## Slide 9
Variable Refrigerant Flow
Water Source Heat Pump
Building overview
Thesis Goals
Depth
Dedicated Outdoor Air System
Variable Refrigerant Flow
Water Source Heat Pump
Air Quality Analysis
Energy Comparison
Structural Breadth
Construction Breadth
Conclusion
Vapor Suction Line
High Pressure Line
Low Pressure Line
Notes: Variable Refrigerant Flow & Water Source Heat Pump
Simultaneous heating & cooling
Eliminates the chiller
Separate zone controls
Uses heat rejected from each space

## Slide 10
Dedicated Outdoor Air System
DOAS Unit | Baseline Design | DOAS Unit | DX Cooling Coil | Natural Gas Coil
 | Supply OA (cfm) | OA Supply (cfm) | Total Capacity (MBH) | Total Capacity (MBH)
L5 AHU | 26,090 | 7,380 | 360 | 80
L6 AHU | 37,075 | 10,366 | 300 | 60
DOAS delivers air directly to the space in VRF system
Enthalpy wheel with general exhaust
WSHP reduces by 32%, VRF reduces by 60%
Chart: Fan Energy
| Baseline | WSHP | VRF
DOAS Energy | 301011.8 | 108468 | 88171.4
Terminal Unit Fan | 61846.7 | 139643.3 | 37378
Building overview
Thesis Goals
Depth
Dedicated Outdoor Air System
Variable Refrigerant Flow
Water Source Heat Pump
Air Quality Analysis
Energy Comparison
Structural Breadth
Construction Breadth
Conclusion

## Slide 11
Variable Refrigerant Flow
Variable Refrigerant Flow With R-410A
Indoor VRF units have the ability to operate as a condenser and a evaporator
Consists of 3 pipes: low pressure, high pressure & vapor suction line
Heat recovery Vs. heat pump
Defrost Operation
Building overview
Thesis Goals
Depth
Dedicated Outdoor Air System
Variable Refrigerant Flow
Water Source Heat Pump
Air Quality Analysis
Energy Comparison
Structural Breadth
Construction Breadth
Conclusion
Vapor Suction Line
High Pressure Line
Low Pressure Line

## Slide 12
ASHRAE 15 Compliance
Institutional Occupancy & Indirect Closed System
Concentration may not exceed 50% listed in table 4-1
Multi-V Refrigerant Charge Calculator
Small rooms use in-duct VRF indoor units
Level 5
Level 6
Building overview
Thesis Goals
Depth
Dedicated Outdoor Air System
Variable Refrigerant Flow
Water Source Heat Pump
Air Quality Analysis
Energy Comparison
Structural Breadth
Construction Breadth
Conclusion
 | OEL (ppm/v/v) | Safety Group | RCL |  |  | Highly Toxic or Toxic Under Code Classification
 |  |  | ppm v/v | lb/Mcf | g/m^3 | 
R-410A | 1,000 | A1 | 140,000 | 13 | 420 | Neither
Zone Configuration | Zone | Outdoor Unit |  | Capacity (tons) | # Indoor Units | RCL (lb/Mcf) | Comply with ASHRAE 15?
 |  | Cooling | Heating |  |  |  | 
Zoning 1 | L5 South Exterior | 264,000 | 297,000 | 22 | 23 | 22.14 | NO
Zoning 2 | L5 South East Ext | 144,000 | 162,000 | 12 | 12 | 19.50 | NO
 | L5 South West Ext | 120,000 | 135,000 | 10 | 11 | 19.76 | NO
Zoning 3 | L5 South West Ext | 96,000 | 108,000 | 8 | 11 | 12.17 | YES
 | L5 S Exterior Zone | 96,000 | 108,000 | 8 | 10 | 12.15 | YES
 | L5 SE Exterior Zone | 96,000 | 108,000 | 8 | 10 | 11.82 | YES
 | L5 SE Corner Zone | 96,000 | 108,000 | 8 | 10 | 11.68 | YES
ASHRAE 15 Refrigerant Charge Limit
Refrigerant Charge Calculations

## Slide 13
ASHRAE 15 Compliance
Institutional Occupancy & Indirect Closed System
Concentration may not exceed 50% listed in table 4-1
Multi-V Refrigerant Charge Calculator
Small rooms use in-duct VRF indoor units
Building overview
Thesis Goals
Depth
Dedicated Outdoor Air System
Variable Refrigerant Flow
Water Source Heat Pump
Air Quality Analysis
Energy Comparison
Structural Breadth
Construction Breadth
Conclusion
 | OEL (ppm/v/v) | Safety Group | RCL |  |  | Highly Toxic or Toxic Under Code Classification
 |  |  | ppm v/v | lb/Mcf | g/m^3 | 
R-410A | 1,000 | A1 | 140,000 | 13 | 420 | Neither
Zone Configuration | Zone | Outdoor Unit |  | Capacity (tons) | # Indoor Units | RCL (lb/Mcf) | Comply with ASHRAE 15?
 |  | Cooling | Heating |  |  |  | 
Zoning 1 | L5 South Exterior | 264,000 | 297,000 | 22 | 23 | 22.14 | NO
Zoning 2 | L5 South East Ext | 144,000 | 162,000 | 12 | 12 | 19.50 | NO
 | L5 South West Ext | 120,000 | 135,000 | 10 | 11 | 19.76 | NO
Zoning 3 | L5 South West Ext | 96,000 | 108,000 | 8 | 11 | 12.17 | YES
 | L5 S Exterior Zone | 96,000 | 108,000 | 8 | 10 | 12.15 | YES
 | L5 SE Exterior Zone | 96,000 | 108,000 | 8 | 10 | 11.82 | YES
 | L5 SE Corner Zone | 96,000 | 108,000 | 8 | 10 | 11.68 | YES
ASHRAE 15 Refrigerant Charge Limit
Refrigerant Charge Calculations

## Slide 14
Zoning
Interior & exterior rooms placed on same system
Zones based on the S Exterior Zone’s outdoor unit’s capacity
Four way cassettes for patient rooms, in-duct for offices
Level 5
Level 6
Building overview
Thesis Goals
Depth
Dedicated Outdoor Air System
Variable Refrigerant Flow
Water Source Heat Pump
Air Quality Analysis
Energy Comparison
Structural Breadth
Construction Breadth
Conclusion
Zone Configuration | Zone | Outdoor Unit |  | Capacity (tons) | # Indoor Units | RCL (lb/Mcf) | Comply with ASHRAE 15?
 |  | Cooling | Heating |  |  |  | 
Zoning 1 | L5 South Exterior | 264,000 | 297,000 | 22 | 23 | 22.14 | NO
Zoning 2 | L5 South East Ext | 144,000 | 162,000 | 12 | 12 | 19.50 | NO
 | L5 South West Ext | 120,000 | 135,000 | 10 | 11 | 19.76 | NO
Zoning 3 | L5 South West Ext | 96,000 | 108,000 | 8 | 11 | 12.17 | YES
 | L5 S Exterior Zone | 96,000 | 108,000 | 8 | 10 | 12.15 | YES
 | L5 SE Exterior Zone | 96,000 | 108,000 | 8 | 10 | 11.82 | YES
 | L5 SE Corner Zone | 96,000 | 108,000 | 8 | 10 | 11.68 | YES

## Slide 15
Sizing
Zone | Critical Load |  | Outdoor Unit |  |  | Number of Units | Max Number
 | Load | MBH | Cooling | Heating | Derated Heating |  | 
L5 NW Exterior Zone | Cooling | 66,238 | 72,000 | 81,000 | 68,850 | 11 | 13
L5 W Interior Zone | Cooling | 55,708 | 72,000 | 81,000 | 68,850 | 13 | 13
L5 SW Exterior Zone | Cooling | 76,585 | 96,000 | 108,000 | 91,800 | 10 | 16
L5 S Exterior Zone | Cooling | 78,562 | 96,000 | 108,000 | 91,800 | 13 | 16
L5 SE Corner Zone | Cooling | 87,183 | 96,000 | 108,000 | 91,800 | 13 | 13
L5 SE Exterior Zone | Cooling | 77,507 | 96,000 | 108,000 | 91,800 | 10 | 16
L5 NE Exterior Zone | Cooling | 51,079 | 72,000 | 81,000 | 68,850 | 13 | 13
L5 NE Interior Zone | Heating | 37,148 | 72,000 | 81,000 | 68,850 | 16 | 16
L6 NW Interior Zone | Cooling | 51,814 | 72,000 | 81,000 | 68,850 | 13 | 13
L6 Interior Zone | Cooling | 52,251 | 72,000 | 81,000 | 68,850 | 12 | 13
L6 E Interior Zone | Cooling | 68,708 | 72,000 | 81,000 | 68,850 | 12 | 13
L6 SW Exterior Zone | Cooling | 68,374 | 72,000 | 81,000 | 68,850 | 13 | 13
L6 S Exterior Zone | Cooling | 45,069 | 72,000 | 81,000 | 68,850 | 13 | 13
L6 SE Exterior Zone | Cooling | 55,377 | 72,000 | 81,000 | 68,850 | 13 | 13
L6 NE Exterior Zone | Cooling | 82,378 | 96,000 | 108,000 | 91,800 | 14 | 16
L6 NW Exterior Zone | Cooling | 59,672 | 72,000 | 81,000 | 68,850 | 9 | 13
Overall 16 Outdoor Condensing Units
Derated heating capacity based on 25°F winter conditions
Max Number of Indoor units for Outdoor unit depends on LG Multi-V
Building overview
Thesis Goals
Depth
Dedicated Outdoor Air System
Variable Refrigerant Flow
Water Source Heat Pump
Air Quality Analysis
Energy Comparison
Structural Breadth
Construction Breadth
Conclusion

## Slide 16
Sizing
Room Name | Sensible from AHU (btu/h) | Room Load (btu/h) | Adjusted (btu/h) | Heating (btu/h) | VRF Indoor Unit |  | WSHP Unit | 
 |  |  |  |  | Cooling | Heating | Cooling | Heating
Medical Bed | 3,169 | 10,528 | 7,359 | 7,270 | 9,600 | 10,900 | 9,700 | 12,000
Medical Bed | 2,868 | 10,528 | 7,659 | 7,270 | 9,600 | 10,900 | 9,700 | 12,000
Medical Bed | 2,868 | 10,528 | 7,659 | 7,270 | 9,600 | 10,900 | 9,700 | 12,000
Medical Bed | 2,868 | 10,528 | 7,659 | 7,270 | 9,600 | 10,900 | 9,700 | 12,000
Medical Bed | 2,868 | 10,528 | 7,659 | 7,270 | 9,600 | 10,900 | 9,700 | 12,000
Medical Bed | 3,169 | 10,528 | 7,359 | 7,270 | 9,600 | 10,900 | 9,700 | 12,000
Pediatric Equipment | 1,036 | 2,649 | 1,613 | 39 | 7,500 | 8,500 | 8,000 | 9,800
Soiled Utility | 216 | 135 | 135 | 0 | 7,500 | 8,500 | 8,000 | 9,800
Nurse Team Center | 1,192 | 2,570 | 1,378 | 40 |  |  |  | 
Remote Monitor Station | 755 | 2,649 | 1,894 | 39 |  |  |  | 
Lab/SAT Poct | 265 | 2,649 | 2,384 | 39 |  |  |  | 
Building overview
Thesis Goals
Depth
Dedicated Outdoor Air System
Variable Refrigerant Flow
Water Source Heat Pump
Air Quality Analysis
Energy Comparison
Structural Breadth
Construction Breadth
Conclusion

## Slide 17
Receptacle & Lighting Dominate Energy
Space Cooling includes both cooling & heating mode
Heat Rejection energy of the condensing unit
VRF consumes 753,443 kwh fewer than Baseline
Chart: Analysis 1: Variable Refrigerant Flow
| Lighting | Heating - Elec | Heating - Gas | Space Cooling | Pumps | Heat Rejection | Fans- Conditioned | Receptacles
VRF | 768.7 | 5.3 | 36 | 730.7 | 0 | 73.3 | 428.5 | 1794.6
Energy Consumption
VRF: Electrical Energy Consumption
Baseline: Electrical Energy Consumption
Building overview
Thesis Goals
Depth
Dedicated Outdoor Air System
Variable Refrigerant Flow
Water Source Heat Pump
Air Quality Analysis
Energy Comparison
Structural Breadth
Construction Breadth
Conclusion
Chart: 
| January | February | March | April | May | June | July | August | September | October | November | December
Lights | 19093.1 | 17247.8 | 19240.4 | 18453.5 | 19166.8 | 18600.8 | 19019.5 | 19240.4 | 18453.5 | 19166.8 | 18527.1 | 19019.5
Miscellaneous Load | 42729 | 38593.9 | 42728.9 | 41350.6 | 42728.9 | 41350.6 | 42728.9 | 42728.9 | 41350.6 | 42728.9 | 41350.6 | 42729
Heat Rejection | 1176.9 | 1158.8 | 1335.3 | 1744.9 | 1980 | 2298.8 | 2574.1 | 2893.5 | 2345.5 | 1728 | 1363.7 | 1414.1
Cooling Mode | 1151.3 | 1665.7 | 2127.8 | 8348.1 | 11343.6 | 21946 | 25321.3 | 26542.8 | 20097 | 5505.6 | 2439.5 | 2535
Heating Mode | 1364.3 | 168.9 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4
Fan Energy | 9774.3 | 9136.3 | 10192.7 | 10314.4 | 11160.5 | 11104.8 | 11428.5 | 11549 | 10831 | 10385 | 9654.9 | 10018.1
Chart: 
| January | February | March | April | May | June | July | August | September | October | November | December
Lights | 19093.1 | 17247.8 | 19240.4 | 18453.5 | 19166.8 | 18600.8 | 19019.5 | 19240.4 | 18453.5 | 19166.8 | 18527.1 | 19019.5
Miscellaneous Load | 42729 | 38593.9 | 42728.9 | 41350.6 | 42728.9 | 41350.6 | 42728.9 | 42728.9 | 41350.6 | 42728.9 | 41350.6 | 42729
Heat Rejection | 6399.9 | 7795.3 | 10122.4 | 12413.2 | 12827 | 12413.2 | 12827 | 12827 | 12413.2 | 12758 | 9775.7 | 10589.4
Chiller | 631.9 | 1425.1 | 1563.6 | 14353.7 | 20574.4 | 30230.1 | 38429 | 39994.6 | 33825.9 | 8708.5 | 2580.3 | 3337.9
Pump Energy | 6959.7 | 6340.2 | 7022 | 7244.1 | 7734.1 | 7960.6 | 8634.1 | 8762.9 | 8183.2 | 7267 | 6839 | 7093
Fan Energy | 52318.5 | 47367.2 | 52112 | 50378.1 | 52317.4 | 50560.9 | 51877.9 | 51889.9 | 50231.5 | 51763.5 | 50092.7 | 51818.3

## Slide 18
Water Source Heat Pump
Water Loop remains between 60°F & 95°F
Uses boiler & cooling tower when it cannot stay in the temperature range
Connects to existing hot water system for 140F minimum flow
All units on same loop, share between offices & patient rooms
Building overview
Thesis Goals
Depth
Dedicated Outdoor Air System
Variable Refrigerant Flow
Water Source Heat Pump
Air Quality Analysis
Energy Comparison
Structural Breadth
Construction Breadth
Conclusion

## Slide 19
Boiler
Gas Fired Hot Water Boiler
Meets peak heating load during winter operation
Primary fuel is Natural Gas, Secondary fuel is fuel oil
All new equipment will be located in central utility plant
Building overview
Thesis Goals
Depth
Dedicated Outdoor Air System
Variable Refrigerant Flow
Water Source Heat Pump
Air Quality Analysis
Energy Comparison
Structural Breadth
Construction Breadth
Conclusion
Equipment Tag | Type | Capacity (Btu/h) | Boiler Horse Power (BHP) | Fluid Flow (gpm) | Primary Fuel | NOX Emissions (ppm)
Boiler - 01 | Gas Fired | 511,011 | 20.0 | 621.0 | Natural Gas | 40

## Slide 20
Cooling Tower
Marley Software used for cooling tower
Design for peak cooling load during summer
Design entering water temperature of 95°F WB
Building overview
Thesis Goals
Depth
Dedicated Outdoor Air System
Variable Refrigerant Flow
Water Source Heat Pump
Air Quality Analysis
Energy Comparison
Structural Breadth
Construction Breadth
Conclusion
Equipment Tag | Design Nominal Tonnage | Motor Hp | Fluid Flow (gpm) | Design Ambient WB (°F) | Design EWT (°F) | Design LWT (°F)
Cooling Tower - 01 | 228.0 | 7.5 | 636 | 78 | 95 | 85

## Slide 21
Water Source Heat Pump
Building overview
Thesis Goals
Depth
Dedicated Outdoor Air System
Variable Refrigerant Flow
Water Source Heat Pump
Air Quality Analysis
Energy Comparison
Structural Breadth
Construction Breadth
Conclusion
Room Name | Sensible from AHU (btu/h) | Room Load (btu/h) | Adjusted (btu/h) | Heating (btu/h) | VRF Indoor Unit |  | WSHP Unit | 
 |  |  |  |  | Cooling | Heating | Cooling | Heating
Medical Bed | 3,169 | 10,528 | 7,359 | 7,270 | 9,600 | 10,900 | 9,700 | 12,000
Medical Bed | 2,868 | 10,528 | 7,659 | 7,270 | 9,600 | 10,900 | 9,700 | 12,000
Medical Bed | 2,868 | 10,528 | 7,659 | 7,270 | 9,600 | 10,900 | 9,700 | 12,000
Medical Bed | 2,868 | 10,528 | 7,659 | 7,270 | 9,600 | 10,900 | 9,700 | 12,000
Medical Bed | 2,868 | 10,528 | 7,659 | 7,270 | 9,600 | 10,900 | 9,700 | 12,000
Medical Bed | 3,169 | 10,528 | 7,359 | 7,270 | 9,600 | 10,900 | 9,700 | 12,000
Pediatric Equipment | 1,036 | 2,649 | 1,613 | 39 | 7,500 | 8,500 | 8,000 | 9,800
Soiled Utility | 216 | 135 | 135 | 0 | 7,500 | 8,500 | 8,000 | 9,800
Nurse Team Center | 1,192 | 2,570 | 1,378 | 40 |  |  |  | 
Remote Monitor Station | 755 | 2,649 | 1,894 | 39 |  |  |  | 
Lab/SAT Poct | 265 | 2,649 | 2,384 | 39 |  |  |  | 

## Slide 22
WSHP: Electrical Energy Consumption
Baseline: Electrical Energy Consumption
Chart: Analysis 2: Water Source Heat Pump
| Lighting | Heating - Elec | Heating - Gas | Space Cooling | Pumps | Heat Rejection | Fans- Conditioned | Receptacles
WSHP | 768.7 | 87.9 | 0 | 757.4 | 14.7 | 41.2 | 890.2 | 1794.6
Energy Consumption
Receptacle & fans dominate energy consumed
Space cooling includes both cooling & heating mode
Heat Rejection energy of the Cooling Tower
WSHP saves over 531,242 kWh than baseline
Building overview
Thesis Goals
Depth
Dedicated Outdoor Air System
Variable Refrigerant Flow
Water Source Heat Pump
Air Quality Analysis
Energy Comparison
Structural Breadth
Construction Breadth
Conclusion
Chart: 
| January | February | March | April | May | June | July | August | September | October | November | December
Lights | 19093.1 | 17247.8 | 19240.4 | 18453.5 | 19166.8 | 18600.8 | 19019.5 | 19240.4 | 18453.5 | 19166.8 | 18527.1 | 19019.5
Miscellaneous Load | 42729 | 38593.9 | 42728.9 | 41350.6 | 42728.9 | 41350.6 | 42728.9 | 42728.9 | 41350.6 | 42728.9 | 41350.6 | 42729
Heat Rejection | 532.5 | 428 | 618.3 | 694.5 | 755.3 | 811.5 | 883.9 | 897.4 | 825.5 | 683 | 610 | 632.3
Cooling Plant | 10898.3 | 12432 | 14731.7 | 18661.5 | 21150.8 | 24173.8 | 26861.6 | 27135.5 | 24664.8 | 16923.4 | 14393.8 | 14391.7
Pump Energy | 366.5 | 331 | 366.5 | 354.7 | 366.5 | 366.5 | 354.7 | 366.5 | 354.7 | 366.5 | 354.7 | 366.5
Fan Energy | 22154.6 | 20102.8 | 22246.2 | 21485.3 | 22430.8 | 21645.5 | 22062.7 | 22072.3 | 21373 | 21971 | 21676.8 | 22014.4
Chart: 
| January | February | March | April | May | June | July | August | September | October | November | December
Lights | 19093.1 | 17247.8 | 19240.4 | 18453.5 | 19166.8 | 18600.8 | 19019.5 | 19240.4 | 18453.5 | 19166.8 | 18527.1 | 19019.5
Miscellaneous Load | 42729 | 38593.9 | 42728.9 | 41350.6 | 42728.9 | 41350.6 | 42728.9 | 42728.9 | 41350.6 | 42728.9 | 41350.6 | 42729
Heat Rejection | 6399.9 | 7795.3 | 10122.4 | 12413.2 | 12827 | 12413.2 | 12827 | 12827 | 12413.2 | 12758 | 9775.7 | 10589.4
Chiller | 631.9 | 1425.1 | 1563.6 | 14353.7 | 20574.4 | 30230.1 | 38429 | 39994.6 | 33825.9 | 8708.5 | 2580.3 | 3337.9
Pump Energy | 6959.7 | 6340.2 | 7022 | 7244.1 | 7734.1 | 7960.6 | 8634.1 | 8762.9 | 8183.2 | 7267 | 6839 | 7093
Fan Energy | 52318.5 | 47367.2 | 52112 | 50378.1 | 52317.4 | 50560.9 | 51877.9 | 51889.9 | 50231.5 | 51763.5 | 50092.7 | 51818.3

## Slide 23
Air Quality Analysis
Baseline CO2 Concentration of 652 ppm
Proposed CO2 Concentration of 912 ppm
OSHA OEL of 5,000 ppm
Building overview
Thesis Goals
Depth
Dedicated Outdoor Air System
Variable Refrigerant Flow
Water Source Heat Pump
Air Quality Analysis
Energy Comparison
Structural Breadth
Construction Breadth
Conclusion
Chart: CO2 Concentration

## Slide 24
Air Quality Analysis
ASHRAE 15 OEL of 1,000 ppm
Passes the oel of R410A within the first hour
Refrigerant leak based on ASHRAE 15 appendix B: Testing
Leak at rate of 2% by mass of the starting charge per hour
Building overview
Thesis Goals
Depth
Dedicated Outdoor Air System
Variable Refrigerant Flow
Water Source Heat Pump
Air Quality Analysis
Energy Comparison
Structural Breadth
Construction Breadth
Conclusion
Chart: R-410A Concentration (ppm)

## Slide 25
Payback Period
Longer payback period for VRF system than WSHP
Similar initial costs for both
Vary within the maintenance costs of larger equipment
20 year life cycle
Chart: Electrical Energy (kWh)
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
Original Design | 123097 | 113479 | 129357 | 140233 | 149528 | 158198 | 169473 | 170534 | 161544 | 137432 | 125813 | 130575
WSHP | 95312 | 89053 | 99535 | 99943 | 105273 | 105394 | 111247 | 111865 | 105520 | 101240 | 96630 | 99761
VRF | 76206 | 68800 | 76562 | 80397 | 86516 | 92444 | 101655 | 103378 | 93263 | 79762 | 74007 | 76411
Building overview
Thesis Goals
Depth
Dedicated Outdoor Air System
Variable Refrigerant Flow
Water Source Heat Pump
Air Quality Analysis
Energy Comparison
Structural Breadth
Construction Breadth
Conclusion
Initial Cost | VRF | WSHP
Expenses / Savings | Additional Costs | Initial Costs
Cooling Tower | -$29,868 | $0
Boiler - 765 MBH | -$17,800 | $0
Outdoor Condensing Unit | $528,000 | $0
Chiller 270 ton | -$190,500 | -$190,500
Terminal Units | $170,825 | $285,600
Piping | $74,176 | $426,920
DOAS Unit | -$361,000 | -$361,000
Costs | $173,833 | $161,020
Maitnenance Costs |  | 
16 Air Cooled Condensers | $138,480 | $0
Cooling Tower | -$8,872 | $0
Chiller - 270 ton | -$104,744 | -$104,744
Boiler - 765 MBH | -$5,835 | $0
Maitnenance Costs | $19,030 | -$104,744
Expenses | $245,596 | $56,276
Annual Energy Costs | $71,763 | $69,108
Simple Payback Period | 3.42 | 0.81
Discounted Payback Period | 8.72 | 2.96
Life Cycle Cost | $2,025,861.00 | $2,631,110.00
Savings | $784,351.66 | $179,102.66

## Slide 26
Energy & Emissions Comparison
Low Nox Burner For Boilers – 30 ppm, 40 ppm For Proposed
VRF Only uses Natural Gas for DOAS unit
WSHP saves 51% on natural gas, VRF saves 72%
Electricity
Consumption
Natural Gas
Consumption
Building overview
Thesis Goals
Depth
Dedicated Outdoor Air System
Variable Refrigerant Flow
Water Source Heat Pump
Air Quality Analysis
Energy Comparison
Structural Breadth
Construction Breadth
Conclusion
Chart: Electrical Energy (kWh)
| Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
Baseline | 123097 | 113479 | 129357 | 140233 | 149528 | 158198 | 169473 | 170534 | 161544 | 137432 | 125813 | 130575
WSHP | 95312 | 89053 | 99535 | 99943 | 105273 | 105394 | 111247 | 111865 | 105520 | 101240 | 96630 | 99761
VRF | 76206 | 68800 | 76562 | 80397 | 86516 | 92444 | 101655 | 103378 | 93263 | 79762 | 74007 | 76411
Chart: Natural Gas (therms)
| Jan | Feb | Mar | April | May | June | July | Aug | Sept | Oct | Nov | Dec
Original | 989 | 409.5 | 350.9 | 223.9 | 12 | 0 | 4.3 | 4.8 | 4.8 | 254.5 | 292.8 | 251.5
WSHP | 649 | 212 | 152 | 39 | 33 | 0 | 0 | 0 | 0 | 61 | 111 | 109
VRF | 101 | 51.4 | 56.9 | 16.1 | 12.7 | 0 | 0 | 0 | 0 | 28.5 | 45.9 | 47.4
Chart: CO2 (lbm/year)
| Baseline | WSHP | VRF
CO2 | 2371616 | 1607903 | 1319577
SO2 | 4515 | 3061 | 2512
NOx | 1556 | 1055 | 866

## Slide 27
Structural Breadth
Cost Savings of $4,248 for reducing load
Original AHUs had 22,000 lb operating weight
Downsized structural system by eliminating anti-force protection & progress collapse resistance loads
Analysis complies with ACI 318 & Direct Design Method
Equipment | Cooling Capacity (Btu/h) | Number | Operating Weight (lb)
Outdoor Condensing Unit | 72,000 | 11 | 4,972
 | 96,000 | 5 | 2,865
L5 DOAS Unit | 360,000 | 1 | 4,284
L6 DOAS Unit | 300,000 | 1 | 4,282
Design | Column Strip |  | Middle Strip | 
 | Neg. Moment | Pos. Moment | Neg. Moment | Pos. Moment
Baseline | 11 (#11) | 18 (#11) | 24 (#6) | 18 (#11)
Reduced Load | 16 (#7) | 18 (#6) | 12 (#6) | 14 (#6)
 | Rebar Size | lb/ft | Number | Weight (lb) | Cost | Total | Savings
Baseline Design | #6 | 1.50 | 24 | 1,219.9 | $1,205 | $7,542 | $4,248
 | #11 | 5.28 | 47 | 8,443.7 | $6,337 |  | 
Proposed Design | #6 | 1.50 | 44 | 2,236.5 | $2,209 | $3,294 | 
 | #8 | 2.66 | 16 | 1,445.8 | $1,085 |  | 
Building overview
Thesis Goals
Depth
Dedicated Outdoor Air System
Variable Refrigerant Flow
Water Source Heat Pump
Air Quality Analysis
Energy Comparison
Structural Breadth
Construction Breadth
Conclusion

## Slide 28
Construction Breadth
Task | Duration - Man Days |  |  |  |  | 
 | Baseline |  | VRF |  | WSHP | 
 | Man - Days | Total Days | Man - Days | Total Days | Man - Days | Total Days
FR&P Interstitial Floors | 79.96 | 10 | 0.00 | 0 | 0.00 | 0
Install Interstitial Floor Deck | 65.36 | 8 | 0.00 | 0 | 0.00 | 0
Install terminal units | 51.00 | 26 | 76.98 | 38 | 76.98 | 38
Piping | 66.29 | 4 | 16.82 | 17 | 12.83 | 13
Sheetmetal | 32.00 | 11 | 21.33 | 11 | 21.33 | 11
 | Total | 58 | Total | 66 | Total | 62
 | Difference in Duration |  |  | -8 |  | -4
Removing IBS floors gained 18 days
Average installation rate of terminal units in a interstitial floor is 30 minutes quicker
Piping Installation does not take interstitial floor into account
Building overview
Thesis Goals
Depth
Dedicated Outdoor Air System
Variable Refrigerant Flow
Water Source Heat Pump
Air Quality Analysis
Energy Comparison
Structural Breadth
Construction Breadth
Conclusion
Removal of IBS Floor |  |  |  |  |  |  | 
Material | Unit | Amount | Crew | Daily Output | Labor-Hours | Total | Total
 |  |  |  |  |  | Incl. O&P | 
W6x20 | ft | 4,148 | 8 | 600 | 0.093 | 43 | $178,364
Floor Decking (3" deep, 18 ga) | sq-ft | 39,304 | 5 | 2850 | 0.011 | 4.29 | $168,614
Polypropylene Fiber Rebar Mat | ft3 | 6,550 | 4 | 9500 | 0.004 | 1.07 | $7,009
LW Concrete, 2-1/2" | sq-ft | 39,304 | 8 | 2585 | 0.022 | 3.3 | $129,703
 |  |  |  |  | Total |  | $483,690
 |  |  |  |  | Entire Building |  | $6,046,125

## Slide 29
Recommendations
Variable Refrigerant Flow
Saves 60% in electrical energy consumption
Consumes 72% less natural gas
Payback period of 8.72 years
Takes 16% longer installation time
Water Source Heat Pump
Saves 31% in electrical energy consumption
Consumes 51% less natural gas
Payback period of 2.96 years
Takes 8% longer installation time
Building overview
Thesis Goals
Depth
Dedicated Outdoor Air System
Variable Refrigerant Flow
Water Source Heat Pump
Air Quality Analysis
Energy Comparison
Structural Breadth
Construction Breadth
Conclusion

## Slide 30
Acknowledgements
Michael Morder
Ashley Hayes
Shawn Manley
Dr. W. Bahnfleth
Penn State Architectural Engineering Faculty
AE Class of 2015
AE Powerplayers
Mechanical Design Engineer, Southland Industries
Project Manager, Southland Industries
Senior Mechanical Engineer, Southland Industries
Thesis Advisor, Professor at Penn State
Photos Courtesy of HKS Inc. and Wingler & Sharp Architects, Inc.
Building overview
Thesis Goals
Depth
Dedicated Outdoor Air System
Variable Refrigerant Flow
Water Source Heat Pump
Air Quality Analysis
Energy Comparison
Structural Breadth
Construction Breadth
Conclusion

## Slide 31
Carl R. Darnall Army Medical Center Replacement
Questions?